## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
2020-21
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4402.65 | 44026.5
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 42.0269 | 202695.6422
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7605.2 | 76052
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2086.23 | 20862.3 | 10 | 2086.23 | 20862.3 | 10 | 2086.23 | 20862.3
5 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 10 | 268.72 | 2687.2 |  |  |  | 10 | 268.72 | 2687.2
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | Pair |  |  |  | 10 | 298.12 | 2981.2
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 347.11 | 3471.1 | 10 | 347.11 | 3471.1 | 10 | 347.11 | 3471.1
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 108.51 | 1085.1 | 10 | 108.51 | 1085.1 | 10 | 108.51 | 1085.1
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 316.82 | 9504.6 | 30 | 316.82 | 9504.6 | 30 | 316.82 | 9504.6
9 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 65.8324 | 204080.44 | 3100 | 65.8324 | 204080.44 | 3100 | 65.8324 | 204080.44
10 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 143.43 | 860.58 | 6 | 143.43 | 860.58 | 6 | 143.43 | 860.58
11 | Stay set 20 mm | 7130860033 | No | 3 | 854.67 | 2564.01 | 3 | 854.67 | 2564.01 | 3 | 854.67 | 2564.01
12 | Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 3 | 268.72 | 806.16 |  |  |  | 3 | 268.72 | 806.16
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 3 | 298.12 | 894.36
13 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 65.9064 | 1680.6129 | 25.5 | 65.9064 | 1680.6129 | 25.5 | 65.9064 | 1680.6129
14 | Concreting of H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / H- Beam pole (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Material cost including GST and labour.
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 151.18 | 211.652 | 6 | 151.18 | 907.08 | 1.4 | 151.18 | 211.652
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 337.79 | 506.685 | 6 | 337.79 | 2026.74 | 1.5 | 337.79 | 506.685
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 69.6311 | 1392.6224 | 20 | 69.6311 | 1392.6224 | 20 | 69.6311 | 1392.6224
18 | Danger Boards | 7130880041 | No | 10 | 82.05 | 820.5 | 10 | 82.05 | 820.5 | 10 | 82.05 | 820.5
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 158.05 | 553.175 | 3.5 | 158.05 | 553.175 | 3.5 | 158.05 | 553.175
20 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  | 69 |  | 0.5 | 69 | 34.5 |  | 69
| 16x65 mm | 7130620614 | Kg |  | 67.85 |  | 7.5 | 67.85 | 508.875 |  | 67.85
| 16x90 mm | 7130620619 | Kg | 3.5 | 67.85 | 237.475 |  | 67.85 |  | 3.5 | 67.85 | 237.475
| 16x140 mm | 7130620625 | Kg |  | 66.7 |  | 10 | 66.7 | 667 |  | 66.7
| 16x160 mm | 7130620627 | Kg | 14.5 | 66.7 | 967.15 |  | 66.7 |  | 14.5 | 66.7 | 967.15
21 | Guarding |  |  |  | 11344.1 |  |  | 11344.1 |  |  | 11344.1
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 57.6636 | 2825.5149 | 49 | 57.6636 | 2825.5149 | 49 | 57.6636 | 2825.5149
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 57.6636 | 1153.2714 | 20 | 57.6636 | 1153.2714 | 20 | 57.6636 | 1153.2714
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 1 | 2965.63 | 2965.63 | 1 | 2965.63 | 2965.63 | 1 | 2965.63 | 2965.63
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 298.12 | 894.36 | 3 | 298.12 | 894.36 | 3 | 298.12 | 894.36
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 66.7 | 80.04 | 1.2 | 66.7 | 80.04 | 1.2 | 66.7 | 80.04
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 123.44 | 493.76 | 4 | 123.44 | 493.76 | 4 | 123.44 | 493.76
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 854.67 | 1709.34 | 2 | 854.67 | 1709.34 | 2 | 854.67 | 1709.34
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 65.9064 | 1120.4086 | 17 | 65.9064 | 1120.4086 | 17 | 65.9064 | 1120.4086
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 67.85 | 101.775 | 1.5 | 67.85 | 101.775 | 1.5 | 67.85 | 101.775
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 313601.9623 |  |  | 492694.5375 |  |  | 360477.4623
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 265764.3748 |  |  | 417537.7437 |  |  | 305489.3748
24 | Incidental Charges @ 7.5% on Sub-Total-1 : - |  |  |  | 0.075 | 23520.1472 |  | 0.075 | 36952.0903 |  | 0.075 | 27035.8097
25 | Labour charges for concreting |  | Cmt | 2 | 642.6794 | 1285.3588 | 8 | 642.6794 | 5141.4353 | 7 | 642.6794 | 4498.7559
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 410.5513 | 4105.5127
27 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 50522.99 | -- | -- | 54612.98 |  |  | 53953.56
28 | Transport charges @ 4% on Column no. 23 |  |  |  |  | 10630.575 |  |  | 16701.5097 |  |  | 12219.575 | NAME CHANGED
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 22, 24, 25, 26, 27, 28 |  |  |  |  | 50458.3182 |  |  | 75762.8191 |  |  | 57273.1454
30 | Total Estimated Cost excluding GST (Row 23, 24, 25, 26, 27, 28, 29) |  |  |  |  | 406287.2768 |  |  | 606708.5781 |  |  | 460470.2207
31 | Applicable CGST @ 9% on Row 30 |  |  |  | 0.09 | 36565.8549 |  | 0.09 | 54603.772 |  | 0.09 | 41442.3199
32 | Applicable SGST @ 9% on Row 30 |  |  |  | 0.09 | 36565.8549 |  | 0.09 | 54603.772 |  | 0.09 | 41442.3199
33 | Total Estimated Cost including GST (Row 30+31+32) |  |  |  |  | 479418.9866 |  |  | 715916.1222 |  |  | 543354.8604
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 479419 |  |  | 715916 |  |  | 543355
Note:
1 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
2 | All the rates are with considering price variation clause.
Note on B54: Barun Chakraborty: Earlier name was - Transport charges upto 50 Kms average lead from area stores to construction camp including site Transport (Trans. Schedule T-1)