## SOR RATE
RATE OF STOCK MATERIALS IN 2015-16
Material Code | Description | unit | Unit rate for 2015-16 | SAP DESCRIPTION
7130200201 | 1:1.5:3 Ratio | Cmt | 4212
7130200202 | 1:3:6 Ratio | Cmt | 3019
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 157 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 268 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Per 1000 | 10423
7130210809 | Aluminium Paint | Ltr. | 290 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 223
7130211158 | Red Oxide Paint | Ltr. | 130 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 225744 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5
7130310007 | 70 Sqmm. | Km. | 73880 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V
7130310008 | 120 Sqmm. | Km. | 92081 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100
7130310020 | 3x400 Sq.mm. | km | 2104858 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 39632 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V
7130310022 | 50 Sqmm. | Km. | 56726 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 59321 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 75464 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 93866 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM
7130310038 | 2.5 Sqmm. | Per Mtr. | 6 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 27 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 55 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 101834 | 11KV PVC INSULATED 150SQMM SINGLE CORE X
7130310042 | 16.0 Sqmm. | km | 66832 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 94953 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | km | 139291
7130310049 | 120 Sq.mm. | km | 401162
7130310050 | 400 Sqmm. | km | 1142914
7130310051 | 3x95 Sq.mm. | km | 841556 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1033058
7130310053 | 3x185 Sq.mm. | km | 1180744 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1501438 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 17336
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 24765
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 287007 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 406042
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 607146
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 572690
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 3784 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 3982 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 50560 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310064 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X35+1X16+1x25 | km | DELETED | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 118163 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 129093 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310067 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x50 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310068 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x70 | km | DELETED
7130310069 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x35+1x70 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 47069 | LT AB CABLEB 3X16+1X25 SQMM
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 60003 | LT AB CABLEB 3X25+1X25 SQMM
7130310075 | 3x240 Sq.mm. | km | 1926090 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 514014.41
7130310077 | 95 Sq.mm | km | 520056 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 775508 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 939613 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1447702 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310652 | 2 Core (UNARMOURED) | Km. | 39708 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. | 78312 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (UNARMOURED) | Km. | 67671 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. | 112811 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310658 | 8 Core (UNARMOURED) | Km. | 125719 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310660 | 10 Core (UNARMOURED) | Km. | 154500 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 172208 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 173129 | CONTROL CABLE COP 12CORE 2.5SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 15990 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 38685 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 52581 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 101586 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 198613 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 247683 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km | 213718 | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC
7130311057 | 150 Sqmm. | km | 412459 | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV
7130311061 | 300 Sqmm. | km | 784944 | Power Cable ARM ALU 3.5CORE 300/150SQMM
7130311084 | 16.0 Sqmm. | km | 99916 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 9906
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 12383 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 14859 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 17336 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 18574
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 22289
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 780 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 842
7130320045 | Cable tie for AB Cable | Each | 25
7130320046 | 11 kV ABC-T Jointing kit 35-70 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 35-70 SQMM
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2396 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2524
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 35084 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 804
7130352031 | 16 Sq.mm, 4 Core | Set | 804 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 863
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1213
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1808
7130352035 | 300 Sq.mm, 3.5 Core | Set | 2923
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3735
7130352037 | End terminating jointing kit for 240 sqmm XLPE cable | Set | 21050 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x70 Sq.mm | Set | 7880
7130352039 | 3x95 Sq.mm | Set | 8701 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 10187 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 10751 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 11000 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 2406 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 2561 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 2630 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box | No. | 3096 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4
7130354277 | 32 Sq mm | Nos. | 5
7130354278 | 50 Sq mm | Nos. | 8 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 13 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 16 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 22 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 25 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 40
7130354284 | 225 Sq mm | Nos. | 46
7130354285 | 240 Sq mm | Nos. | 66
7130354286 | 300 Sq mm | Nos. | 77 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 100
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 627 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 80 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 104 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 145 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 149 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 172 | STRAIGHT THROUGH JOINT
7130390008 | Piercing connector for services 16-50 Sq. mm Tap off 2.5-16 Sq. mm | Each | DELETED
7130390017 | Suspension Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390018 | Tension/Dead end Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390019 | End cap for 50/70 Sq.mm | Nos. | 28 | END CLAMP CAP FOR 50/70 SQMM
7130600023 | 50 x 50 x 6 mm | MT | 40214 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 40214 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 40214 | M S ANGLE 75X75X6 MM
7130600075 | Angle line Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing kit 11KV ABC Cabl 3x25+1x35sqmm
7130600166 | 75x40 mm | MT | 40214 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 40214 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 40214 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 40214 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 44989 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 44989 | R S JOIST 175X85 MM
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 47741 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 47741 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 44989 | H BEAMS 152X152MM; 37,1 KG/MTR.
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 44989 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR
7130610206 | Barbed wire | MT | 66528 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 118 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 64
7130620133 | 16x40 mm | Kg | 89 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 89 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 64 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 65 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 65 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 64 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 63 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 63 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 62 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 62 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 62 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 395 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 127 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 mm cable of dia 105 mm | RM | 929 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 805 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3220 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | 600 mm | Each | 3857
7130640036 | 900 mm | Each | 7661 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG)
7130640037 | M.S.Pipe 200 mm dia with collars | RM (light) | 918 | M.S. PIPE 200MM DIA WITH COLLARS
7130641396 | Gl Pipe 40 mm | Per Mtr | 190 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 820 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4169 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2 | Sq.mtr | 1131
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 119
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 599 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 435 | SUSPENSION CLAMP
7130797533 | Suspension Clamp (Suitable for all size cable) | Each | DELETED | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 1654 | PCC POLE 140 KG; 8,0 MTR LONG
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each | 6408
7130800033 | 280 Kg; 9.1 Mtr long | Each | 3129 | PCC POLE 280 KG; 9,1 MTR LONG
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each | 10737 | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT
7130800672 | 350 Kg; 7.0 Mtr long | Each | 2851 | PCC POLE 350 KG; 7,0 MTR LONG
7130810005 | Through Bolt | No | 83 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 6808 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 142 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 265 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 71 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 68 | Strain Plate
7130810077 | Pole Clamp | No. | 394 | POLE CLAMP
7130810102 | Service Ring | No. | 349 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 265 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 282 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 282 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 282 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 282 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 618 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 736 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 854 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 1048 | 11 KV V CROSS ARM
7130810509 | Lightning Arrestor Structure | No. | 7845 | D.O. / LA Mounting channel 75x40 mm.
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 3322 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2485 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 3940 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2862 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4022 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 4547 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2332 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5377 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 90 | STRAIN PLATE
7130810624 | Strain Plate | Set | 94 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 388 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 294 | 11KV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3227 | 11KV cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 8457 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 294 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 157 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 388 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 140 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 354 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 3 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 412 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1907 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 31
7130820030 | Disc insulator | Each | 231 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 40 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 230 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 9 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 10 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 9 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 60 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 199 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 32 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 30 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 34 | HARDWARE FOR 75X90MM LTSHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 123 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 255 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2183 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 139 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km | 11084 | CONDUCTOR AAA SQURREL
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km | 17295 | CONDUCTOR AAA WEASEL
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km | 27240 | CONDUCTOR AAA RABBIT
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 33968 | CONDUCTOR AAA RACOON
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 32 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 126 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 534
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 13002 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq)
7130830054 | Bimetallic clamp for VCB | Each | 312
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 20281 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq)
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 312
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 33544 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q)
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 158
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 50002 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 64842 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq)
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 167935 | CONDUCTOR ACSR PANTHER 130 sq mm
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 50246 | CONDUCTOR AAA DOG
7130830585 | T-Clamp for Dog Conductor. | Each | 239 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 191 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 279 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 232 | Bimetallic clamps for transformer &kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 26 | SLEEVE JOINTING ALUMINIUM FOR 0.03SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 195 | SLEEVE REPAIR ALUMINIUM FOR .2SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 3483 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 425 | LIGHTNING ARRESTORS11 KV gapless type.
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 4547 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4393 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 100 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 387 | STAY SET WITHOUT STAY WIRE16mm Paint11KV
7130860033 | Stay Set 20 mm (Painted) | Each | 705 | STAY SET WITHOUT STAY WIRE 20mm (Painted
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 61002 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 61600 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 681
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 100 | EARTHING COIL 8SWG GI WIRE 50MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 371 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 55133 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 55094 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 55094 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 1930
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 1003 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877679 | Section Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing Kit 11 kV ABC Section Suspensio
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2270 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2018 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 113 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 124 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 74 | 7130880041Danger boards 33KV & 11 KV.
7130890003 | M.S. sheet meter piller box | Each | DELETED | M.S. SHEET METER PILLER BOX
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 4543 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 5733
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 13002 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 13621 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 51 | LT LINE SPACERS
7130890009 | GSM Modem | Nos. | 4017 | GSM MODEM
7130893004 | Eye Hook | No. | 161 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3315 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 106
7131210846 | Metal Halide light lamp | No. | DELETED | LAMP METAL HALIDE 250W
7131210852 | CFL 7 Watts | Each | 97
7131210881 | 250 Watt Metal Halide | Each | 1260 | METAL HALIDE LAMP 250 WATT
7131220182 | Tube Light Rod (T5 type) | Each | 52 | LAMPS: -Tube Light (40 Watts.)
7131230003 | 250 Watt Sodium Vapour | Each | 470 | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER
7131230116 | 250 Watt Mercury Vapour | Each | 370 | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each | 1967 | S/ V HIGH PRESSURE LAMP 400W 230/250V
7131280006 | CFL 15 Watts | Each | 103
7131280007 | CFL 20 Watts | Each | 135 | CFL 20 WATTS LAMP
7131280008 | CFL 23 Watts | Each | 174
7131280009 | 125 Watt Mercury Vapour | Each | 161
7131280010 | Halogen Filament (1000 Watts) | Each | 99
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each | 6502
7131280012 | Street Light fitting with tube light | Each | 650 | STREET LIGHT FITTING WITH TUBE LIGHT
7131280013 | Street Light fitting with CFL | Each | 2718 | STREET LIGHT FITTING WITH CFL
7131280014 | HPSV lamp 150 watt | Each | 325 | HPSV LAMP 150 WATT
7131280015 | HPSV Choke 250 watt | Each | 1355 | HPSV LAMP 250 WATT
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each | 3100 | 150 WATT METAL HALIDE HPSV FITTING
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each | 3874 | 250 WATT METAL HALIDE HPSV FITTING
7131280882 | CFL 11 Watts | Each | 97
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 2326 | ENERGY METER ENECTRONIC 10-60 AMPS
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for 132 kV) | Each | 1039058 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 178
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 648 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 975 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A
7131300881 | CMRI | Each | 50063 | Common Meter Reading Instrument CMRI
7131310013 | 3 Ø 4 Wire 0.5S Non DLMS | Each | 4030 | HT TRIVECTOR METER 5 AMPS
7131310015 | CT operated electronic static meters with AMR (Composite Unit). | Each | 11297 | ELECTORNIC LTCT METER 3X4 100/5 A
7131310033 | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | Each | 3970 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310034 | 3 Ø 4 Wire 0.5S with DLMS Protocol category B | Each | 4030 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310035 | 3 Ø 3 Wire 0.2S Non DLMS | Each | 16362 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC (
7131310036 | 3 Ø 4 Wire 0.2S Non DLMS | Each | 16362 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC (
7131310037 | Test terminal Box (TTB) | Each | 870 | TTB
7131310994 | Three Phase, 20-100 Amps. with Meter Box with data storage. | Each | 2618 | LT ELEC.STATIC METER3X4X20-100A WITHLUGS
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 2487 | 3 PHASE 4 WIRE LTCT OPERATED METER
7131320009 | Digital Multimeter Electronic Type | Nos. | 2700 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) | Nos. | 3940
7131324780 | Megger 500 V | Nos. | 3240
7131324806 | Megger up to 2.5 kV | Nos. | 4883 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6842
7131334001 | Set of 3 O.C. relays instantaneous high set feature | Nos. | 7851 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH | Old Bin Code 7131329276
7131334002 | Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature | Nos. | 7278 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO | Old Bin Code 7131329277
7131399007 | Master trip relays | Nos. | 1585 |  | Old Bin Code 7131329278
7131338004 | Transil oil Dielectric Breakdown testkit | Nos. | 64638
7131338025 | Neon tester | Nos. | 51 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 216
7131387502 | Thermometer (Wall Mounted) | Nos. | 427 | THERMOMETER (WALL MOUNTED)
7131390009 | Piercing connector suitable for 16 Sq.mm-95 Sq.mm AB Cable-Service connections | Nos. | DELETED
7131390010 | Piercing connector for Main 16-50 Sq. mm Tap off 16-50 Sq. mm. | Each | DELETED
7131390012 | Piercing connector suitable for 25 Sq.mm-95 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390013 | Piercing connector suitable for 50 Sq.mm-150 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390014 | Earthing Coil for messenger wire | Nos. | 169
7131390015 | Anchor sleeve for messenger wire | Nos. | 31
7131390016 | Universal hook & Bolts & nuts | Nos. | 420
7131820031 | LT Single Phase MCB 5 Amps. | Each | 101
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 101 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 430
7131820034 | LT Three Phase MCB 32 Amps. | Each | 430
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 2865
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3104
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3104
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2268
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5193 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900005 | Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base). | Each | 2114 | LT ROBUST POLE FUSE UNIT
7131900005 |  |  | 2603 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 283 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 435 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 13 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 14 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 279 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 109 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 701 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 775 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 684 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 683 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 681 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 674 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 671 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 671 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 672 | FUSE WIRE TINNED COPPER 10 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 44 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 87 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 25 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 269 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 534 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 964 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920112 | 11 kV Kiosk VCB | Each | 248028 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 681 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1634 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3161 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 4438 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 6021 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 9095 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  | 51.2435
7131920767 | Distribution Board with MCB | No. | DELETED | DIST.BOARD & DP MCB 4NO 6A&2NO 16A
7131930109 | 33 kV ; 600 Amps with earth switch. | Each | 40392 | 33 KV 600AMPS WITH EARTH SWITCH ISOLATO
7131930221 | 11 kV Porcelain A.B. Switch | Each | 7750 | AB Switch with complete fitting 11 KV
7131930221 | Single phase AB switch complete. | Set | 12911 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 18624 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1199 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2918 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 20680 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 35789 | 33 KV Isolator 800A without earth switch
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2387 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 22680 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 22680
7131941762 | 11 kV VCB without control panel & CT's. | Each | 110737 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 226584 | 33KV VCB FOR 30 VOLT DC
7131950009 | Distribution box 1 ph. 4 connectors | Each | DELETED | DISTRIBUTION BOX 1 PH 4 CONNECTOR
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1147 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950011 | Distribution box 3 phase 2 connectors | Each | DELETED | DISTRIBUTION BOX 3 PH 2 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1355 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950013 | Spring loaded distribution box for service connection with stainless steel buckle. | Each | DELETED | SPRING LOADED DIST. BOX FOR SERVICE CONN
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 57208
7131950016 | 11 kV Sectionalizer. | Each | 345600
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 13758 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 17198 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 34396 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 45861 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 26078 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 28850 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 26331 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 26995 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960520 | 2 Feeder Control (Static Relays) | Each | 39700 | 11KV MULTICIRCUIT(2F) CONTROL PANNELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 39815 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 39815 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm;3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 184
7132004003 | Hack saw frames + B185 | Nos. | 119
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 10
7132013331 | Discharge Rod | Nos. | 515 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 2700
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 989
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 306
7132061858 | Combination Plier | Nos. | 204 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 66 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 62 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 57 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. | 743 | SCREW DRIVER INSULATED 255MM
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1430 | RING SPANNER
7132074033 | Tube Spanners | Set. | 591
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 676 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 439
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F& tommy Bar) | Set. | 1303 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1086
7132088615 | Pipe Wrench 18 inches size | Nos. | 596
7132200014 | 1089 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 | Each | 135369 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 1628 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3254 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3910 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 6490 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 179001 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each | 44836 | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each | 54268 | TRANSFORMER 25KVA 11/0.4KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | 88254 | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | Not Procured | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each | 119054 | TRANSFORMER 100KVA 11/0.43KV FOUR STAR
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each | 220748 | TRANSFORMER 200KVA 11/0.4KV FOUR STAR
7132210012 | 315 kVA (CEA Design) | Each | 423239 | XMER 315KVA 11/0.43KV CEA REG. CU WOUND
7132210077 | 5 kVA Single Phase | Each | 25351 | TRANSFORMER 11/.4KV 5 KVA 1 PHASE
7132210078 | 10 kVA Single Phase | Each | 36194 | TRANSFORMER 11/.4KV 10 KVA 1 PHASE
7132210079 | 16 kVA (3 Star) Copper Wound | Each | DELETED | TRANSFORMER 11/.4KV 16 KVA 3 PHASE COPPE
7132210107 | Single Phase transformer with protection (16 kVA) | No | DELETED | Single Ph transfor with protection 16KVA
7132210108 | 25 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 25 KVA 3 STAR RATING
7132210109 | 25 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/.4 KV 25 KVA
7132210116 | 63 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 63 KVA 3 STAR RATING
7132210117 | 100 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 100 KVA 3 STAR RATIN
7132210118 | 200 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/.4KV 200 KVA 3 STAR RATIN
7132210120 | 200 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/0.4 KV 200 KVA
7132210125 | 315 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/0.4 KV 315 KVA
7132210127 | 500 kVA (Conventional) | Each | 538012 | TRANSFORMER 11/0.4 KV 500 KVA
7132210215 | 50 kVA (Copper winding) | Each | 146905 | TRANSFORMER 33/.4KV 50KVA
7132210231 | 63 kVA (Conventional) | Each | DELETED | TRANSFORMER 33/0.4 KV 200 KVA
7132210234 | 100 kVA (Conventional) | Each | DELETED | TRANSFORMER 33/0.4 KV 300 KVA
7132220091 | Power Transformer 1600 kVA | Each | 841136 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 3150 kVA | Each | 2112952 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 3010759 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 241090 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 335 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 222386 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 335 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 268 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 268 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1 | No. | 460044 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 18227 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1 | No. | 290795 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1 | No. | 331734 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1 | No. | 735218 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1 | No. | 484141 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1 | No. | 448513 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 30290
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 67155 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 8903 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 8903 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 18948 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5) Amps oil filled | Each | 16868 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each | 16544 | 33KV CT's (100-50/5)A oil filled OD Type
7132230330 | 132 kV C.T. 100-50/1 | No. | 328366 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1 | No. | 304009 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1 | No. | 266309 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each | 35395 | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 31841 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each | 31131 | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 30287 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 30894 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each | 30894 | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 29949 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 30894 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 64587 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each | 77029 | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each | 64768 | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 66527 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 66527 | OIL IMM 3 PH CTPT UNITS 33 KV-100&200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 64768 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 66145 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 8903 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN | Old Bin Code-7132230472
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16371 | VOLTAGE TRANSFORMER 33KV/110VOLTS SINGLE | Old Bin Code-7132230482
7132230501 | 132 kV P.T. | No. | 227961 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 540886 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132404015 | Safety belts | Nos. | 549 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 123 | SAFETY HELMETS
7132404366 | Battery (Low Maintenance SAN controller) | No. | 49161 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 131 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2437 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406425 | Universal Meter Box for HT meters. | Each | 2528 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2538 | LTCT METER WITH DLMS
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 457 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5166 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 771 | RAIN COATS WITH HOODS
7132427635 | Gum Boots | Nos. | 519 | GUM BOOTS
7132438002 | Silica gel | Kg | 163 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 4 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Earthing Rods) | Set. | 893
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 3710 | METTING RUBBER 1900X1800X12MM | Old Bin Code-7132448851
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 274
7132457798 | Transformer Oil In Barrel | KL | 77842 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 68897 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 5 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1020 | HDPE PIPE 200MM ID; 240MM OD
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 371 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 9316 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 310
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 131
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 15 | PVC INSULATION TAPES 19 MM WIDE AND IN R
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 71
7132478004 | Tong tester | Nos. | 1351 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 534
7132478012 | Hand Torch 3 cell | Nos. | 364 | HAND TORCH 3 CELLED
7132478012 | Cotton Waste | Kg | 65 | HAND TORCH 3 CELLED
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 4619 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 59
7132490053 | Bitumen compound | Kg | 90
7132498006 | River sand | Cmt | 650 | RIVER SAND

## D-1
COST SCHEDULE D-1
LT LINE 3 PHASE 5 WIRE ON PCC SUPPORTS USING RABBIT / WEASEL / SQUIRREL CONDUCTORS WITH MAXIMUM SPAN OF 60 METERS
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 50 Sqmm ACSR & 2 Wires of 20 Sqmm |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 3 Wires of 30 Sqmm ACSR & 2 Wires of 20 Sqmm ACSR |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
1 | 140 Kg, 8.0 Mtr. long PCC support | 7130800012 | No | 1654 | 17 | 28118 | 17 | 28118 | 17 | 28118 | 17 | 28118 | 17 | 28118
2 | LT Five Pin Cross arm | 7130810461 | No | 854 | 22 | 18788 | 22 | 18788 | 22 | 18788 | 22 | 18788 | 22 | 18788
3 | LT Shackle insulator (90x75 mm) including cut point/angle location | 7130820106 | No | 10 | 88 | 880 | 88 | 880 | 88 | 880 | 88 | 880 | 88 | 880
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 34 | 30 | 1020 | 30 | 1020 | 30 | 1020 | 30 | 1020 | 30 | 1020
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 32 | 17 | 544 | 17 | 544 | 17 | 544 | 17 | 544 | 17 | 544
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.544 | 4120 | 138201.28 | 3090 | 103650.96 | -- |  | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.281 | -- |  | -- |  | 4120 | 83557.72 | 3090 | 62668.29 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 13.002 | 1030 | 13392.06 | 2060 | 26784.12 | 1030 | 13392.06 | 2060 | 26784.12 | 5150 | 66960.3
7 | (i) Stay set 16 mm | 7130860032 | No | 387 | 9 | 3483 | 9 | 3483 | 9 | 3483 | 9 | 3483 | 9 | 3483
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 61.6 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4
| (iii) Stay Clamp | 7130810026 | No | 142 | 9 | 1278 | 9 | 1278 | 9 | 1278 | 9 | 1278 | 9 | 1278
| (iv) Stay Insulator | 7130820117 | No | 9 | 9 | 81 | 9 | 81 | 9 | 81 | 9 | 81 | 9 | 81
8 | Split insulator for guarding | 7130820018 | No | 3 | 44 | 132 | 44 | 132 | 44 | 132 | 44 | 132 | 44 | 132
9 | Binding wire and tape | 7130830006 | Kg | 139 | 3.5 | 486.5 | 3.5 | 486.5 | 3.5 | 486.5 | 3.5 | 486.5 | 3.5 | 486.5
10 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 551.2 | 2954.432 | 551.2 | 2954.432 | 551.2 | 2954.432 | 551.2 | 2954.432 | 551.2 | 2954.432
11 | Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 64 | 10 | 640 | 10 | 640 | 10 | 640 | 10 | 640 | 10 | 640
| 16x40 mm | 7130620609 | Kg | 64 | 5 | 320 | 5 | 320 | 5 | 320 | 5 | 320 | 5 | 320
| 16x140 mm | 7130620625 | Kg | 62 | 20 | 1240 | 20 | 1240 | 20 | 1240 | 20 | 1240 | 20 | 1240
12 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 5 | 500 | 5 | 500 | 5 | 500 | 5 | 500 | 5 | 500
13 | Red Oxide Paint | 7130211158 | Ltr | 130 | 2 | 260 | 2 | 260 | 2 | 260 | 2 | 260 | 2 | 260
14 | Aluminium Paint | 7130210809 | Ltr | 290 | 2 | 580 | 2 | 580 | 2 | 580 | 2 | 580 | 2 | 580
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 55.094 | 6 | 330.564 | 6 | 330.564 | 6 | 330.564 | 6 | 330.564 | 6 | 330.564
16 | SUB TOTAL-1 |  |  |  |  | 216555.236 |  | 195396.976 |  | 161911.676 |  | 154414.306 |  | 131922.196
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 19489.9712 |  | 17585.7278 |  | 14572.0508 |  | 13897.2875 |  | 11872.9976
18 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 138.8677 | 17 | 2360.751 | 17 | 2360.751 | 17 | 2360.751 | 17 | 2360.751 | 17 | 2360.751
19 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 2.65 | 7866.4216 | 2.65 | 7866.4216 | 2.65 | 7866.4216 | 2.65 | 7866.4216 | 2.65 | 7866.4216
20 | Labour charges as per Sch No. DL-1 |  |  |  |  | 37870.48 |  | 37870.48 |  | 37870.48 |  | 37870.48 |  | 37870.48
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 9382.77 |  | 9382.77 |  | 9382.77 |  | 9382.77 |  | 9382.77
22 | SUB TOTAL-2 |  |  |  |  | 293525.6298 |  | 270463.1264 |  | 233964.1494 |  | 225792.0161 |  | 201275.6162
23 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 23821.076 |  | 21493.6674 |  | 17810.2844 |  | 16985.5737 |  | 14511.4416
24 | Total cost per Km for non-guaranteed works |  |  |  |  | 317346.7057 |  | 291956.7937 |  | 251774.4337 |  | 242777.5897 |  | 215787.0577
25 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 317347 |  | 291957 |  | 251774 |  | 242778 |  | 215787
Note :- All the rates are with considering price variation clause.

## D-2
COST SCHEDULE D-2
1 Km LT LINES 3 Phase 4 Wire USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
2015-16
S. NO. | PARTICULARS | New Bin Code | Unit | Rate | Using 50 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 1654 | 17 | 28118 | 17 | 28118 | 17 | 28118
2 | LT Four Pin cross arm | 7130810441 | No | 736 | 22 | 16192 | 22 | 16192 | 22 | 16192
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 10 | 66 | 660 | 66 | 660 | 66 | 660
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 32 | 17 | 544 | 17 | 544 | 17 | 544
5 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 34 | 25 | 850 | 25 | 850 | 25 | 850
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.544 | 3090 | 103650.96 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.281 | -- |  | 3090 | 62668.29 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 13.002 | 1030 | 13392.06 | 1030 | 13392.06 | 4120 | 53568.24
7 | (i) Stay set 16 mm | 7130860032 | No | 387 | 9 | 3483 | 9 | 3483 | 9 | 3483
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 61.6 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4
| (iii) Stay Clamp | 7130810026 | No | 142 | 9 | 1278 | 9 | 1278 | 9 | 1278
| (iv) Stay Insulator | 7130820117 | No | 9 | 9 | 81 | 9 | 81 | 9 | 81
8 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad. |  | Cmt 1:3:6
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 551.2 | 2954.432 | 551.2 | 2954.432 | 551.2 | 2954.432
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 5 | 500 | 5 | 500 | 5 | 500
10 | Split insulator for guarding | 7130820018 | Pair | 3 | 44 | 132 | 44 | 132 | 44 | 132
11 | M.S. Nuts and Bolts |  | Kg |  | 35 |  | 35 |  | 35
| 12x100 mm | 7130620573 | Kg | 64 | 10 | 640 | 10 | 640 | 10 | 640
| 16x40 mm | 7130620609 | Kg | 64 | 5 | 320 | 5 | 320 | 5 | 320
| 16x140 mm | 7130620625 | Kg | 62 | 20 | 1240 | 20 | 1240 | 20 | 1240
12 | Binding wire and tape | 7130830006 | Kg | 139 | 3.5 | 486.5 | 3.5 | 486.5 | 3.5 | 486.5
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 2 | 580 | 2 | 580 | 2 | 580
14 | Red Oxide paint | 7130211158 | Ltr | 130 | 2 | 260 | 2 | 260 | 2 | 260
15 | GI wire 8 SWG for guarding | 7130870043 | Kg | 55.094 | 6 | 330.564 | 6 | 330.564 | 6 | 330.564
16 | SUB TOTAL-1 |  |  |  |  | 179018.916 |  | 138036.246 |  | 115544.136
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 16111.7024 |  | 12423.2621 |  | 10398.9722
18 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 138.8677 | 17 | 2360.751 | 17 | 2360.751 | 17 | 2360.751
19 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 2.65 | 7866.4216 | 2.65 | 7866.4216 | 2.65 | 7866.4216
20 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 35623.42 |  | 35623.42 |  | 35623.42
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 9382.77 |  | 9382.77 |  | 9382.77
22 | SUB TOTAL-2 |  |  |  |  | 250363.981 |  | 205692.8707 |  | 181176.4708
23 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 19692.0808 |  | 15183.9871 |  | 12709.855
24 | Total cost per Km for non-guaranteed works |  |  |  |  | 270056.0617 |  | 220876.8577 |  | 193886.3257
25 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 270056 |  | 220877 |  | 193886
Note:- All the rates are with considering price variation clause.

## D-3
COST SCHEDULE D-3
1 Km LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON 140 Kg; 8.0 Mtr. LONG PCC SUPPORTS WITH MAXIMUM SPAN OF 60 METERS
2015-16
S. No. | PARTICULARS |  | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | PCC Pole 140 Kg, 8.0 Mtr long | 7130800012 | No | 1654 | 17 | 28118 | 17 | 28118 | 17 | 28118
2 | LT Three Pin cross arm | 7130810413 | No | 618 | 22 | 13596 | 22 | 13596 | 22 | 13596
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 10 | 44 | 440 | 44 | 440 | 44 | 440
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 32 | 22 | 704 | 22 | 704 | 22 | 704
5 | Hardware for 90x75 mm Shackle insu. | 7130820216 | No | 34 | 25 | 850 | 25 | 850 | 25 | 850
6 | ACSR conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.544 | 1030 | 34550.32 | -- |  | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.281 | 1030 | 20889.43 | 2060 | 41778.86 | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 13.002 | 1030 | 13392.06 | 1030 | 13392.06 | 3090 | 40176.18
7 | (i) Stay set 16 mm | 7130860032 | No | 387 | 9 | 3483 | 9 | 3483 | 9 | 3483
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 61.6 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4
| (iii) Stay Clamp | 7130810026 | No | 142 | 9 | 1278 | 9 | 1278 | 9 | 1278
| (iv) Stay Insulator | 7130820117 | No | 9 | 9 | 81 | 9 | 81 | 9 | 81
8 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad. |  | Cmt 1:3:6
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 551.2 | 2954.432 | 551.2 | 2954.432 | 551.2 | 2954.432
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 5 | 500 | 5 | 500 | 5 | 500
10 | Split insulator for guarding | 7130820018 | Pair | 3 | 44 | 132 | 44 | 132 | 44 | 132
11 | M.S. Nuts and Bolts |  | Kg |  | 16 |  | 16 |  | 16
| 12x100 mm | 7130620573 | Kg | 64 | 3.5 | 224 | 3.5 | 224 | 3.5 | 224
| 16x40 mm | 7130620609 | Kg | 64 | 1.5 | 96 | 1.5 | 96 | 1.5 | 96
| 16x140 mm | 7130620625 | Kg | 62 | 11 | 682 | 11 | 682 | 11 | 682
12 | Binding wire and tape | 7130830006 | Kg | 139 | 3.5 | 486.5 | 3.5 | 486.5 | 3.5 | 486.5
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 1.5 | 435 | 1.5 | 435 | 1.5 | 435
14 | Red Oxide paint | 7130211158 | Ltr | 130 | 1.5 | 195 | 1.5 | 195 | 1.5 | 195
15 | GI wire 4 mm for guarding | 7130870043 | Kg | 55.094 | 6 | 330.564 | 6 | 330.564 | 6 | 330.564
16 | SUB TOTAL-1 |  |  |  |  | 126743.706 |  | 113082.816 |  | 98088.076
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 11406.9335 |  | 10177.4534 |  | 8827.9268
18 | Back filling of pole pit with boulder @ 0.25 Cmt |  | No | 138.8677 | 17 | 2360.751 | 17 | 2360.751 | 17 | 2360.751
19 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 2.65 | 7866.4216 | 2.65 | 7866.4216 | 2.65 | 7866.4216
20 | Labour charges as per Sch No. DL-1 |  |  |  |  | 33376.36 |  | 33376.36 |  | 33376.36
21 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 9930.0982 |  | 9930.0982 |  | 9930.0982
22 | SUB TOTAL-2 |  |  |  |  | 191684.2703 |  | 176793.9002 |  | 160449.6336
23 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 13941.8077 |  | 12439.1098 |  | 10789.6884
24 | Total cost per Km for non-guaranteed works |  |  |  |  | 205626.078 |  | 189233.01 |  | 171239.322
25 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 205626 |  | 189233 |  | 171239
Note: | All the rates are with considering price variation clause.

## D-4
COST SCHEDULE D-4
2015-16
1 KM OF 3 PHASE 5 WIRE LT LINE ON R.S. JOIST WITH ACSR CONDUCTOR FOR URBAN AREAS
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 3 Ph, 5 Wire line on RSJ 125x70 mm 9.3 Mtr long with max. span 45 Mtrs for size of conductor upto 3x50 Sqmm + 2x30 Sqmm ACSR |  | 3Ph, 5 Wire line on RSJ 175x85 mm 9.3 Mtr long with max. span 65 Mtrs for size of conductor upto 3x80 Sqmm + 2x30 Sq mm ACSR
[5 empty] | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | (i) R.S. Joist (125x70 mm) 9.3 Mtr long @13.198 Kg = 122.74 kg/pole x 22 No = 2700.28 Kgs | 7130600635 | Kg | 44.989 | 2700.28 | 121482.8969 | -- | --
| (ii) R.S. Joist (175x85 mm) 9.3 Mtr long @ 19.495 Kg per mtr x 9.3 mtr = 181.3 Kg/pole x 15 No = 2719.55 Kgs | 7130600675 | Kg | 44.989 | -- | -- | 2719.55 | 122349.835
2 | LT Five Pin Cross arm | 7130810461 | No | 854 | 27 | 23058 | 20 | 17080
3 | LT Shackle Insulator (90x75 mm) including cut point/angle location | 7130820106 | No | 10 | 108 | 1080 | 80 | 800
4 | Hardware for 90x75 mm shackle insulator | 7130820216 | No | 34 | 35 | 1190 | 35 | 1190
5 | Earth knob (Aluminium bobbin) | 7130820201 | No | 32 | 27 | 864 | 20 | 640
6 | ACSR conductor including 3% sag
| (i) 80 Sqmm Al. Eq (Raccoon) | 7130830060 | Mtr | 50.002 | -- |  | 3090 | 154506.18
| (ii) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.544 | 3090 | 103650.96 | --
| (iii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.281 | 2060 | 41778.86 | 2060 | 41778.86
7 | (i) Stay set 16 mm | 7130860032 | No | 387 | 12 | 4644 | 12 | 4644
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704 | 12 | 1704
8 | Split insulator for guarding | 7130820018 | Pair | 3 | 60 | 180 | 40 | 120
9 | Binding wire and tape | 7130830006 | Kg | 139 | 3.5 | 486.5 | 3 | 417
10 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & support @ 0.3 Cmt |  | Cmt 1:3:6 |  | 10.1 |  | 7.65
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 2100 | 11256 | 1591 | 8527.76
11 | M.S. Nuts and Bolts |  | Kg |  | 44 |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 17 | 1088 | 12 | 768
| 16x40 mm | 7130620609 | Kg | 64 | 8 | 512 | 5 | 320
| 16x65 mm | 7130620614 | Kg | 63 | 19 | 1197 | 13 | 819
12 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 7 | 700 | 5 | 500
13 | Red Oxide Paint | 7130211158 | Ltr | 130 | 5 | 650 | 5 | 650
14 | Aluminium Paint | 7130210809 | Ltr | 290 | 5 | 1450 | 5 | 1450
15 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 55.094 | 7.5 | 413.205 | 5 | 275.47
16 | SUB TOTAL-1 |  |  |  |  | 321820.6219 |  | 362975.305
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 28963.856 |  | 32667.7774
18 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 10.1 | 29981.4559 | 7.65 | 22708.7265
19 | Labour charges as per Sch. No. DL-2 |  |  |  |  | 49043.97 |  | 41798.03
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 9044.6521 |  | 9044.6521
21 | SUB TOTAL-2 |  |  |  |  | 438854.5559 |  | 469194.491
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 35400.2684 |  | 39927.2835
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 474254.8243 |  | 509121.7746
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 474255 |  | 509122
Note:- All the rates are with considering price variation clause.

## D-5
COST SCHEDULE D-5
1 Km. LT LINE 1 PHASE 3 WIRE USING RABBIT / WEASEL / SQUIRREL CONDUCTORS ON RSJ SUPPORTS WITH MAXIMUM SPAN OF 45 METERS FOR URBAN AREAS
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | Using one wire of 50 Sqmm, one wire of 30 Sqmm ACSR and one wire of 20 Sqmm ACSR Conductor |  | Using 30 Sqmm as Phase & 20 Sqmm ACSR as neutral |  | Using 20 Sqmm ACSR as Phase & neutral
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 125x70 mm 9.3 Mtr long RSJ supports @ 13.198 Kg/mtr = 122.74 Kg/pole x 22 Nos = 2700.28 Kgs. | 7130600635 | Kg | 44.989 | 2700.28 | 121482.8969 | 2700.28 | 121482.8969 | 2700.28 | 121482.8969
2 | LT Three Pin cross arm | 7130810413 | No | 618 | 22 | 13596 | 22 | 13596 | 22 | 13596
3 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 10 | 54 | 540 | 54 | 540 | 54 | 540
4 | Earth knob (Aluminium bobbin) | 7130820201 | No | 32 | 22 | 704 | 22 | 704 | 22 | 704
5 | Hardware for 90x75 mm shackle insul. | 7130820216 | No | 34 | 22 | 748 | 22 | 748 | 22 | 748
6 | ACSR Conductor including 3% sag
| (i) 50 Sqmm Al. Eq (Rabbit) | 7130830057 | Mtr | 33.544 | 1030 | 34550.32 | -- | -- | -- | --
| (ii) 30 Sqmm Al. Eq (Weasel) | 7130830055 | Mtr | 20.281 | 1030 | 20889.43 | 2060 | 41778.86 | -- | --
| (iii) 20 Sqmm Al. Eq (Squirrel) | 7130830053 | Mtr | 13.002 | 1030 | 13392.06 | 1030 | 13392.06 | 3090 | 40176.18
7 | (i) Stay set 16 mm | 7130860032 | No | 387 | 9 | 3483 | 9 | 3483 | 9 | 3483
| (ii) Stay Wire 7/10 SWG @ 6 Kg/Stay | 7130860077 | Kg | 61.6 | 54 | 3326.4 | 54 | 3326.4 | 54 | 3326.4
| (iii) Stay Clamp | 7130810026 | No | 142 | 9 | 1278 | 9 | 1278 | 9 | 1278
8 | Concreting of stay & base pad for pole @ 0.2 Cmt/stay and @ 0.05 Cmt for base pad & support @ 0.3 Cmt. |  | Cmt 1:3:6
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 2100 | 11256 | 2100 | 11256 | 2100 | 11256
9 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 7 | 700 | 7 | 700 | 7 | 700
10 | Split insulator for guarding | 7130820018 | Pair | 3 | 60 | 180 | 60 | 180 | 60 | 180
11 | M.S.Nuts and Bolts |  | Kg |  | 20 |  | 20 |  | 20
| 12x100 mm | 7130620573 | Kg | 64 | 7 | 448 | 7 | 448 | 7 | 448
| 16x40 mm | 7130620609 | Kg | 64 | 3 | 192 | 3 | 192 | 3 | 192
| 16x65 mm | 7130620614 | Kg | 63 | 10 | 630 | 10 | 630 | 10 | 630
12 | Binding wire and tape | 7130830006 | Kg | 139 | 3 | 417 | 3 | 417 | 3 | 417
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 5 | 1450 | 5 | 1450 | 5 | 1450
14 | Red Oxide Paint | 7130211158 | Ltr | 130 | 5 | 650 | 5 | 650 | 5 | 650
15 | G.I. Wire 8 SWG for guarding | 7130870043 | Kg | 55.094 | 5 | 275.47 | 5 | 275.47 | 5 | 275.47
16 | SUB TOTAL-1 |  |  |  |  | 230188.5769 |  | 216527.6869 |  | 201532.9469
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20716.9719 |  | 19487.4918 |  | 18137.9652
18 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 10.1 | 29981.4559 | 10.1 | 29981.4559 | 10.1 | 29981.4559
19 | Labour charges as per Sch. No. DL-1 |  |  |  |  | 33376.36 |  | 33376.36 |  | 33376.36
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 9044.6521 |  | 9044.6521 |  | 9044.6521
21 | SUB TOTAL-2 |  |  |  |  | 323308.0169 |  | 308417.6468 |  | 292073.3802
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 25320.7435 |  | 23818.0456 |  | 22168.6242
23 | Total cost per Km for non-guaranteed works |  |  |  |  | 348628.7603 |  | 332235.6923 |  | 314242.0043
24 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 348629 |  | 332236 |  | 314242

## D-6 (1)
COST SCHEDULE -- D-6 (1)
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST/H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support |  |  |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No =3626.07 Kgs |  |  |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos= 4081 Kgs
[5 empty] | Using 1100 V grade AB Cable 3x50 + 1x25 + 1x35 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x50 + 1x25 + 1x35 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm. |  | Using 1100 V grade AB Cable 3x50 + 1x25 + 1x35 sqmm. |  | Using 1100 V grade AB Cable 3x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 6 | 7 | 8 | 9 | 6 | 7 | 8 | 9
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.989 |  |  |  |  | 3626.07 | 163133.2632 | 3626.07 | 163133.2632
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 44.989 | [8 empty] | 6678 | 300436.542 | 6678 | 300436.542
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 1654 | 20 | 33080 | 20 | 33080
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 435 | 22 | 9570 | 22 | 9570 | 22 | 9570 | 22 | 9570 | 22 | 9570 | 22 | 9570 | Earlier- Suspension clamp assembly 25 to 95 sq.mm bare messenger
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 80 | 30 | 2400 | 30 | 2400 | 30 | 2400 | 30 | 2400 | 30 | 2400 | 30 | 2400 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-for street light
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 104 | 45 | 4680 | 45 | 4680 | 45 | 4680 | 45 | 4680 | 45 | 4680 | 45 | 4680 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-Distribution Box (3 Nos. per 3 phase DB & 1 No. per 1 phase DB)
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 145 | 24 | 3480 | 24 | 3480 | 24 | 3480 | 24 | 3480 | 24 | 3480 | 24 | 3480 | Earlier- Piercing connector suitable for AB Cable to AB Cable Tee connections.
4 | Universal distribution connector | 7130390006 | Each | 149 | 41 | 6109 | 41 | 6109 | 41 | 6109 | 41 | 6109 | 41 | 6109 | 41 | 6109
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 599 | 22 | 13178 | 22 | 13178 | 22 | 13178 | 22 | 13178 | 22 | 13178 | 22 | 13178 | Earlier- Dead-end Assembly (Suitable for all size cable)
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size
(a) | 3x50 + 1x25 + 1x35 sqmm. (6% sag) | 7130310066 | Mtr | 129.093 | 1100 | 142002.3 |  |  | 1100 | 142002.3 |  |  | 1100 | 142002.3
(b) | 3x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310032 | Mtr | 75.464 |  |  | 1100 | 83010.4 |  |  | 1100 | 83010.4 |  |  | 1100 | 83010.4
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 12 | 4644 | 12 | 4644 | 12 | 4644 | 12 | 4644 | 12 | 4644 | 12 | 4644
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2 | 72 | 4435.2 | 72 | 4435.2 | 72 | 4435.2 | 72 | 4435.2 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704 | 12 | 1704 | 12 | 1704 | 12 | 1704 | 12 | 1704 | 12 | 1704
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole i.e. 8.4 Cmt for RSJ & 12.4 Cmt for H-Beam pole |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 707 | 3789.52 | 707 | 3789.52 | 1747 | 9363.92 | 1747 | 9363.92 | 2579 | 13823.44 | 2579 | 13823.44
9 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30 |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128 | 2 | 128 | 2 | 128 | 2 | 128 | 2 | 128 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896 | 14 | 896 | 14 | 896 | 14 | 896 | 14 | 896 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882 | 14 | 882 | 14 | 882 | 14 | 882 | 14 | 882 | 14 | 882
10 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 20 | 2000 | 20 | 2000 | 20 | 2000 | 20 | 2000 | 20 | 2000 | 20 | 2000
11 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1355 | 15 | 20325 | 15 | 20325 | 15 | 20325 | 15 | 20325 | 15 | 20325 | 15 | 20325
12 | Stainless steel strap with buckle for installation of Service Distribution Box. |  | Set | 57 | 15 | 855 | 15 | 855 | 15 | 855 | 15 | 855 | 15 | 855 | 15 | 855
13 | Red Oxide Paint | 7130211158 | Ltr | 130 | 5 | 650 | 5 | 650 | 20 | 2600 | 20 | 2600 | 20 | 2600 | 20 | 2600
14 | Aluminium Paint | 7130210809 | Ltr | 290 | 5 | 1450 | 5 | 1450 | 20 | 5800 | 20 | 5800 | 20 | 5800 | 20 | 5800
15 | Pole Clamp | 7130810077 | No | 394 | 44 | 17336 | 44 | 17336 | 44 | 17336 | 44 | 17336 | 44 | 17336 | 44 | 17336
16 | Eye Hook | 7130893004 | No | 161 | 44 | 7084 | 44 | 7084 | 44 | 7084 | 44 | 7084 | 44 | 7084 | 44 | 7084
17 | Service Ring | 7130810102 | No | 349 | 30 | 10470 | 30 | 10470 | 30 | 10470 | 30 | 10470 | 30 | 10470 | 30 | 10470
18 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 15.99 | 90 | 1439.1 | 90 | 1439.1 | 90 | 1439.1 | 90 | 1439.1 | 90 | 1439.1 | 90 | 1439.1
19 | Straight through joints | 7130390007 | No | 172 | 8 | 1376 | 8 | 1376 | 8 | 1376 | 8 | 1376 | 8 | 1376 | 8 | 1376
20 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 20 | 560 | 20 | 560 | 20 | 560 | 20 | 560 | 20 | 560 | 20 | 560
21 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 530 | 2650 | 530 | 2650 | 530 | 2650 | 530 | 2650 | 530 | 2650 | 530 | 2650
22 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 66.528 | 70 | 4656.96 | 70 | 4656.96 | 70 | 4656.96 | 70 | 4656.96 | 70 | 4656.96 | 70 | 4656.96
23 | Back Clamp for Pole
| (i) Stay Clamp for R.S. Joist | 7130810216 | No | 282 |  |  |  |  | 40 | 11280 | 40 | 11280
| (ii) Stay Clamp for "H" Beam | 7130810692 | No | 294 | [8 empty] | 40 | 11760 | 40 | 11760
24 | SUB TOTAL-1 |  |  |  |  | 301830.08 |  | 242838.18 |  | 455037.7432 |  | 396045.8432 |  | 597280.542 |  | 538288.642
25 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 27164.7072 |  | 21855.4362 |  | 40953.3969 |  | 35644.1259 |  | 53755.2488 |  | 48445.9778
26 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 187.2721 | 20 | 3745.4427 | 20 | 3745.4427
27 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 3.4 | 10092.7673 | 3.4 | 10092.7673 | 8.4 | 24935.0722 | 8.4 | 24935.0722 | 12.4 | 36808.9162 | 12.4 | 36808.9162
28 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 40323.47 |  | 40323.47 |  | 46430.65 |  | 46430.65 |  | 48696.74 |  | 48696.74
29 | Transportation charges |  |  |  |  | 11038.5501 |  | 11038.5501 |  | 12059.5331 |  | 12059.5331 |  | 12059.5331 |  | 12059.5331
30 | SUB TOTAL-2 |  |  |  |  | 394195.0173 |  | 329893.8463 |  | 579416.3955 |  | 515115.2245 |  | 748600.9801 |  | 684299.8091
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 33201.3088 |  | 26712.1998 |  | 50054.1518 |  | 43565.0428 |  | 65700.8596 |  | 59211.7506
32 | Total cost per Km for non-guaranteed works |  |  |  |  | 427396.3261 |  | 356606.0461 |  | 629470.5473 |  | 558680.2673 |  | 814301.8397 |  | 743511.5597
33 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 427396 |  | 356606 |  | 629471 |  | 558680 |  | 814302 |  | 743512
Note:- All the rates are with considering price variation clause.

## D-6 (2)
COST SCHEDULE -- D-6 (2)
1 KM OF 3 PHASE 5 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS. AND R.S. JOIST/H-BEAM POLE SUPPORT USING AB XLPE CABLE WITH MAXIMUM SPAN 50 METER URBAN AREA
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | RS Joist (175X85) mm 9.3 Mtr Long i.e. 19.495 kg/mtr x 9.3 mtr = 181.30 kg x 20 No = 3626.07 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm. |  | H-BEAM 152x152 mm 37.1 Kg/Mtr 9.0 Mtr long i.e. 408.1 Kg/pole x10 Nos = 4081 Kgs Using 1100 V grade AB Cable 3x70 + 1x16 + 1x50 sqmm.
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 6 | 7 | 6 | 7
1(a) | RS Joist (175X85) mm 9.3 Mtr Long i.e.19.495 kg/mtr x 9.3 mtr=181.30 kg x 20 No = 3626.07 Kgs | 7130600675 | Kg | 44.989 |  |  | 3626.07 | 163133.2632
(b) | H-BEAM 152x152 mm 37.1 Kg /Mtr 9.0 Mtr long i.e. 333.9 Kg/pole x 20 Nos = 6678 Kgs | 7130601958 | Kg | 44.989 |  |  |  |  | 6678 | 300436.542
(c) | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 1654 | 20 | 33080
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 435 | 22 | 9570 | 22 | 9570 | 22 | 9570 | Earlier- Suspension clamp assembly 25 to 95 sq.mm bare messenger
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 80 | 30 | 2400 | 30 | 2400 | 30 | 2400 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-for street light
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 104 | 45 | 4680 | 45 | 4680 | 45 | 4680 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-Distribution Box (3 Nos. per 3 phase DB & 1 No. per 1 phase DB)
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 145 | 24 | 3480 | 24 | 3480 | 24 | 3480 | Earlier- Piercing connector suitable for AB Cable to AB Cable Tee connections.
4 | Universal distribution connector | 7130390006 | Each | 149 | 41 | 6109 | 41 | 6109 | 41 | 6109
5 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 599 | 22 | 13178 | 22 | 13178 | 22 | 13178 | Earlier- Dead-end Assembly (Suitable for all size cable)
6 | LT 3 phase 5 Wire Aerial Bunched Cable of Size
(a) | 3x70 + 1x16 + 1x50 sqmm. (6% sag) | 7130300025 | Mtr | 225.744 | 1100 | 248318.4 | 1100 | 248318.4 | 1100 | 248318.4
7 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 12 | 4644 | 12 | 4644 | 12 | 4644
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2 | 72 | 4435.2 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704 | 12 | 1704 | 12 | 1704
8 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole i.e. 8.4 Cmt for RSJ & 12.4 Cmt for H-Beam pole |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 707 | 3789.52 | 1747 | 9363.92 | 2579 | 13823.44
9 | M.S. Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128 | 2 | 128 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896 | 14 | 896 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882 | 14 | 882 | 14 | 882
10 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 20 | 2000 | 20 | 2000 | 20 | 2000
11 | Distribution box 3 phase 5 connectors | 7131950012 | No | 1355 | 15 | 20325 | 15 | 20325 | 15 | 20325
12 | Stainless steel strap with buckle for installation of Service Distribution Box. |  | No | 57 | 15 | 855 | 15 | 855 | 15 | 855
13 | Red Oxide Paint | 7130211158 | Ltr | 130 | 5 | 650 | 20 | 2600 | 20 | 2600
14 | Aluminium Paint | 7130210809 | Ltr | 290 | 5 | 1450 | 20 | 5800 | 20 | 5800
15 | Pole Clamp | 7130810077 | No | 394 | 44 | 17336 | 44 | 17336 | 44 | 17336
16 | Eye Hook | 7130893004 | No | 161 | 44 | 7084 | 44 | 7084 | 44 | 7084
17 | Service Ring | 7130810102 | No | 349 | 30 | 10470 | 30 | 10470 | 30 | 10470
18 | PVC insulated single core 16 sq.mm. cable @ 6 mtr. per 3 phase box | 7130311008 | Mtr | 15.99 | 90 | 1439.1 | 90 | 1439.1 | 90 | 1439.1
19 | Straight through joints | 7130390007 | No | 172 | 8 | 1376 | 8 | 1376 | 8 | 1376
20 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 20 | 560 | 20 | 560 | 20 | 560
21 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 530 | 2650 | 530 | 2650 | 530 | 2650
22 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 66.528 | 70 | 4656.96 | 70 | 4656.96 | 70 | 4656.96
23 | Back Clamp for Pole
| (i) Stay Clamp for R.S. Joist | 7130810216 | No | 282 |  |  | 40 | 11280
| (ii) Stay Clamp for "H" Beam | 7130810692 | No | 294 |  |  |  |  | 40 | 11760
24 | SUB TOTAL-1 |  |  |  |  | 408146.18 |  | 561353.8432 |  | 703596.642
25 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 36733.1562 |  | 50521.8459 |  | 63323.6978
26 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 187.2721 | 20 | 3745.4427
27 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 3.4 | 10092.7673 | 8.4 | 24935.0722 | 12.4 | 36808.9162
28 | Labour charges as per Sch. No.- DL-7 |  |  |  |  | 40323.47 |  | 46430.65 |  | 48696.74
29 | Transportation charges |  |  |  |  | 11038.5474 |  | 12059.5284 |  | 12059.5284
30 | SUB TOTAL-2 |  |  |  |  | 510079.5636 |  | 695300.9397 |  | 864485.5243
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 44896.0798 |  | 61748.9228 |  | 77395.6306
32 | Total cost per Km for non-guaranteed works |  |  |  |  | 554975.6434 |  | 757049.8625 |  | 941881.1549
33 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 554976 |  | 757050 |  | 941881
Note:- All the rates are with considering price variation clause.

## D-6 (3)
COST SCHEDULE -- D-6 (3)
1 KM OF 1 PHASE 3 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS.
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 1x25 + 1x16 + 1x25 sqmm.
[5 empty] | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 1654 | 20 | 33080
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 435 | 22 | 9570 | Earlier- Suspension clamp assembly
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 80 | 30 | 2400 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-for street light
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 104 | 20 | 2080 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-Distribution Box (3 Nos. per 3 phase DB & 1 No. per 1 phase DB)
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 145 | 24 | 3480 | Earlier- Piercing connector suitable for AB Cable to AB Cable Tee connections.
4 | Distribution box 1 phase 9 connectors | 7131950010 | Each | 1147 | 20 | 22940
5 | Universal distribution connector | 7130390006 | No | 149 | 41 | 6109
6 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 599 | 22 | 13178 | Earlier- Dead-end Assembly (Suitable for all size cable)
7 | LT 1 phase 3 Wire AB XLPE Cable 1x25 + 1x16 + 1x25 sqmm. (6% sag) | 7130310063 | Mtr | 50.56 | 1100 | 55616
8 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 12 | 4644
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704
9 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole i.e. 8.4 Cmt for RSJ & 12.4 Cmt for H-Beam pole |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 707 | 3789.52
10 | M.S. Nuts and Bolts |  | Kg |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882
11 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 6 | 600
12 | Stainless steel strap with buckle for installation of Service Distribution Box. |  | Set | 57 | 20 | 1140
13 | Red Oxide Paint | 7130211158 | Ltr | 130 | 3 | 390
14 | Aluminium Paint | 7130210809 | Ltr | 290 | 3 | 870
15 | Pole Clamp | 7130810077 | No | 394 | 44 | 17336
16 | Eye Hook | 7130893004 | No | 161 | 44 | 7084
17 | Service Ring | 7130810102 | No | 349 | 30 | 10470
18 | PVC insulated single core 16 sq.mm. cable @ 3 mtr. per 1 phase box | 7130311008 | Mtr | 15.99 | 60 | 959.4
19 | Straight through joints | 7130390007 | No | 172 | 10 | 1720
20 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 10 | 280
21 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 530 | 2650
22 | Barbed wire [@ 2 kg per pole] | 7130610206 | Kg | 66.528 | 70 | 4656.96
23 | SUB TOTAL-1 |  |  |  |  | 213088.08
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 19177.9272
25 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 187.2721 | 20 | 3745.4427
26 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 3.4 | 10092.7673
27 | Labour charges as per schedule DL-8 |  |  |  |  | 35903.79
28 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 11038.5474
29 | SUB TOTAL-2 |  |  |  |  | 293046.5546
30 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 23439.6888
31 | Total cost per Km for non-guaranteed works |  |  |  |  | 316486.2434
32 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 316486
Note:- All the rates are with considering price variation clause.

## D-6 (4)
COST SCHEDULE -- D-6 (4)
1 Km. OF 3 PHASE 4 WIRE LT LINE WITH AERIAL BUNCH CABLE FOR PUMP CONNECTION UPTO 5 HP & 5 CONNECTION PER KM. WITH MAXIMUM SPAN 50 MTRS.
2015-16
Sl. No. | Particulars | New Bin Code | Unit | Rate (Rs.) | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm.
[5 empty] | Qty. | Amt (Rs.)
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg., 8.0 Mtrs. long PCC Poles | 7130800012 | No. | 1654 | 20 | 33080
2 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No. | 100 | 6 | 600
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No. | 80 | 30 | 2400 |  | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 104 | 15 | 1560 |  | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-Distribution Box (3 Nos. per 3 phase DB & 1 No. per 1 phase DB)
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 145 | 24 | 3480 |  | Earlier- Piercing connector suitable for AB Cable to AB Cable Tee connections.
4 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3x16 + 1x25 sqmm. (6% sag) | 7130310070 | Mtr | 47.069 | 1100 | 51775.9
5(i) | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet | 7130890007 | Each | 13621 | 1 | 13621
(ii) | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | Each | 1355 | 5 | 6775
6 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 12 | 4644
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704
7 | Concreting of stay @ 0.2 Cmt/stay ; concreting of piller box @ 0.5 Cmt per box and concreting of base pad for pole @ 0.05 Cmt/pole. |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 811.2 | 4348.032
8 | M.S. Nuts and Bolts
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882
9 | Universal distribution connector | 7130390006 | Each | 149 | 41 | 6109
10 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 435 | 22 | 9570 | Earlier- Suspension clamp assembly 25 to 95 sq.mm bare messenger
11 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 599 | 22 | 13178 | Earlier- Dead-end Assembly (Suitable for all size cable)
12 | Red Oxide Paint | 7130211158 | Ltr | 130 | 1 | 130
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 1 | 290
14 | Pole Clamp | 7130810077 | No | 394 | 44 | 17336
15 | Eye Hook | 7130893004 | No | 161 | 44 | 7084
16 | Service Ring | 7130810102 | No | 349 | 30 | 10470
17 | Straight through joints | 7130390007 | No | 172 | 6 | 1032
18 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 20 | 560
19 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 530 | 2650
20 | SUB TOTAL-1 |  |  |  |  | 198738.132
21 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 17886.4319
22 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 187.2721 | 20 | 3745.4427
23 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 3.9 | 11576.9978
24 | Labour charges as per Sch. No.- DL-9 |  |  |  |  | 40978.93
25 | Transportation charges |  |  |  |  | 11038.5501
26 | SUB TOTAL-2 |  |  |  |  | 283964.4845
27 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 21861.1945
28 | Total cost per Km for non-guaranteed works |  |  |  |  | 305825.679
29 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 305826

## D-6 (A)
COST SCHEDULE -- D - 6 (A)
1 KM OF 3 PHASE 5 WIRE LINE USING AB XLPE CABLE (BY REPLACEMENT OF EXISTING BARE LT CONDUCTOR) FOR URBAN AREA
Based on COST SCHEDULE D-6
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | RS Joist (175X85) mm 9.3 Mtr Long Using 1100 V grade AB Cable 3x50 + 1x25 + 1x35 sqmm.
[5 empty] | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1(i) | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No. | 435 | 20 | 8700 | Earlier- Suspension clamp assembly
(ii) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No. | 80 | 100 | 8000 | Earlier- Piercing connector 50 Sqmm
(iii) | Universal distribution connector | 7130390006 | No. | 149 | 20 | 2980
(v) | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No. | 599 | 10 | 5990 | Earlier- Dead-end Assembly (Suitable for all size cable)
2 | LT AB Cable 3x50 + 1x25 + 1x35 sqmm. (6% sag) | 7130310066 | Mtr | 129.093 | 1060 | 136838.58
3 | M.S.Nuts and Bolts |  | Kg |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882
4 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 20 | 2000
5 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | No | 1355 | 20 | 27100
6 | Pole Clamp | 7130810077 | No | 394 | 25 | 9850
7 | Eye Hook | 7130893004 | No | 161 | 25 | 4025
8 | Service Ring | 7130810102 | No | 349 | 20 | 6980
9 | PVC insulated single core 16 sq.mm. cable | 7130311008 | Mtr | 15.99 | 200 | 3198
10 | Straight through joints | 7130390007 | No | 172 | 20 | 3440
11 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 20 | 560
12 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130320053 | No | 5 | 530 | 2650
13 | SUB TOTAL-1 |  |  |  |  | 224217.58
14 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20179.5822
15 | Labour charges as per Sch. No.DL-6(A) |  |  |  |  | 28867.43
16 | Transportation charges |  |  |  |  | 5040.336
17 | SUB TOTAL-2 |  |  |  |  | 278304.9282
18 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 24663.9338
19 | Dismantling Charges (50% of labour charges) |  |  |  |  | 14433.715
20 | Total cost per Km |  |  |  |  | 317402.577
21 | Total cost per Km (R/Off) |  |  |  |  | 317403

## D-6 (B)
COST SCHEDULE -- D-6 (B)
COST SCHEDULE FOR ADDITIONAL POLES (MID SPAN) FOR LT LINE WITH AB CABLE
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Qnty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RSJ (125x70 mm) 9.3 Mtr long @ 13.198 kg | 7130600635 | Kg | 122.74 | 44.989 | 5521.9499
2 | Concreting of Pole @ 0.05 Cmt for base pad and support @ 0.3 Cmt per pole |  | Cmt | 0.35
| Cement @ 208 kg per Cmt | 7130200401 | Kg | 72.8 | 5.36 | 390.208
3 (i) | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 1 | 435 | 435 | Earlier- Suspension clamp assembly
(ii) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 4 | 80 | 320 | Earlier- Piercing connector
(iii) | Universal distribution connector (1 No. per pole) | 7130390006 | No | 1 | 149 | 149
4 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | 7131950012 | No | 1 | 1355 | 1355
5 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 1 | 100 | 100
6 | SUB TOTAL-1 |  |  |  |  | 8271.1579
7 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 744.4042
8 | Service in lieu of concreting metal & sand only |  | Cmt | 0.35 | 2968.461 | 1038.9613
9 | Labour charges [as per Sch. No.- DL-6(B)] |  |  |  |  | 1323.89
10 | Transportation charges |  |  |  |  | 551.9076
11 | SUB TOTAL-2 |  |  |  |  | 11930.321
12 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 909.8274
13 | Total Cost per |  |  |  |  | 12840.1484
14 | Total cost (R/Off) |  |  |  |  | 12840

## D-7
COST SCHEDULE D-7
HVDS SYSTEM OF 200 kVA PARENT DTR TAKING 4 Km. LT. TO BE CONVERTED.
2015-16
S. No. | PARTICULARS | Bin Code | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 25 kVA 11/0.4 kV Transformer 4 STAR | 7132210008 | No | 54268 | 5 | 271340
2 | 16 kVA 11/0.4 kV conventional Transformer (4 STAR Aluminium Wound) | 7132210007 | No | 44836 | 4 | 179344
3 | 10 kVA 11/0.4 kV SINGLE PHASE Transformer | 7132210078 | No | 36194 | 4 | 144776
4 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 1654 | 10 | 16540
5 | (i) Stay Set 16 mm | 7130860032 | No | 387 | 40 | 15480
| (ii) Stay Wire 7/10 SWG (5.5 Kg/stay) | 7130860077 | Kg | 61.6 | 220 | 13552
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | No | 142 | 40 | 5680
6 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4547 | 11 | 50017
7 | D.O. mounting Channel | 7130810509 | Set | 3322 | 11 | 36542
8 | DC Channel 100x50x6 mm | 7130850201 | Set | 4547 | 11 | 50017
9 | 11 kV Single pole cut point fitting | 7130810681 | No | 3227 | 10 | 32270
10 | 11 kV Strain Hardware set | 7130820241 | No | 123 | 60 | 7380
11 | 11 kV Polymer Disc Insulator | 7130820010 | No | 140 | 60 | 8400 | Earlier- 11 kV Disc Insulator
12 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 425 | 33 | 14025 | Earlier- 11 kV L.A. set
13 | 11 kV D.O. Fuse Unit | 7131930412 | No | 1199 | 33 | 39567
14 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter. |  | No | 16000 | 7 | 112000
15 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter. |  | No | 13000 | 4 | 52000
16 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 39.632 | 220 | 8719.04
17 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 94.953 | 10400 | 987511.2
18 | G.I. Pipe 40 mm (9 Mtr. per sub-station) | 7130641396 | Mtr | 190 | 99 | 18810
19 | G.I. Wire 8 SWG | 7130870043 | Kg | 55.094 | 660 | 36362.04
20 | 11 kV 'V' Cross arm | 7130810495 | No | 1048 | 65 | 68120
21 | 11 kV Top Clamp | 7130810679 | No | 294 | 65 | 19110
22 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 157 | 195 | 30615 | Earlier- 11 kV Pin Insulator
23 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 65 | 6500
24 | M.S. Nuts and Bolts |  | Kg |  | 320
| 16x40 mm | 7130620609 | Kg | 64 | 50 | 3200
| 16x65 mm | 7130620614 | Kg | 63 | 100 | 6300
| 16x90 mm | 7130620619 | Kg | 63 | 20 | 1260
| 16x140 mm | 7130620625 | Kg | 62 | 50 | 3100
| 16x160 mm | 7130620627 | Kg | 62 | 50 | 3100
| 16X200 mm | 7130620631 | Kg | 62 | 50 | 3100
25 | Concreting of stay @ 0.2 Cmt/stay |  | Cmt
| (i) Cement @ 208 Kg/cmt | 7130200401 | Kg | 5.36 | 1664 | 8919.04
26 | I- Bolt 16 mm | 7130860017 | No | 100 | 77 | 7700
27 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.281 | 1200 | 24337.2
28 | SUB TOTAL-1 |  |  |  |  | 2285693.52
29 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 205712.4168
30 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 138.8677 | 10 | 1388.677
31 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 8 | 23747.6879
32 | Labour charges [as per Sch. No.- DL-10] |  |  |  |  | 143003.14
33 | Transportation charges |  |  |  |  | 9382.7711
34 | SUB TOTAL-2 |  |  |  |  | 2668928.2128
35 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 251426.2872
36 | Total cost per Km for non-guaranteed works |  |  |  |  | 2920354.5
37 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 2920355
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-8
COST SCHEDULE D-8
HVDS SYSTEM OF 100 kVA PARENT DTR TAKING 3 KM. LT TO BE CONVERTED
2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 25 kVA 11/0.4 kV Transformer 4 STAR | 7132210008 | No. | 54268 | 2 | 108536
2 | 16 kVA 11/0.4 kV conventional Transformer (4 STAR Aluminium Wound) | 7132210007 | kg | 44836 | 3 | 134508
3 | 10 kVA 11/0.4 kV SINGLE PHASE Transformer | 7132210078 | No. | 36194 | 3 | 108582
4 | 140 Kg 8 Mtr. Long PCC pole (for mid span) | 7130800012 | No. | 1654 | 8 | 13232
5 | (i) Stay Set 16 mm | 7130860032 | No | 387 | 30 | 11610
| (ii) Stay Wire 7/10 (5.5 kg/stay) | 7130860077 | Kg | 61.6 | 165 | 10164
| (iii) Stay Clamp for 140 kg PCC | 7130810026 | No | 142 | 30 | 4260
6 | Transformer mounting cross arm DC channel 100x50x6 mm. 2.7 mtr long 8' centre | 7130850201 | Set | 4547 | 7 | 31829
7 | DC Cross arm 100x50x6 mm 8 ' centre 2.7 mtr long | 7130850201 | Set | 4547 | 7 | 31829
8 | DO mounting Channel | 7130810509 | Set | 3322 | 11 | 36542
9 | 11 kV Single pole cut point channel | 7130810681 | No | 3227 | 10 | 32270
10 | 11 kV Strain Hardware set | 7130820241 | No. | 123 | 48 | 5904
11 | 11 kV Polymer Disc Insulator | 7130820010 | No | 140 | 48 | 6720 | Earlier- 11 kV Disc Insulator
12 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 425 | 21 | 8925 | Earlier- 11 kV L.A. set
13 | 11 kV D.O. Set | 7131930412 | No | 1199 | 21 | 25179
14 | Protection cum metering box with 40 amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 3 | 48000
15 | Protection cum metering box with 25 amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 4 | 52000
16 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 39.632 | 140 | 5548.48
17 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 94.953 | 1820 | 172814.46
18 | G.I. Pipe 40 mm (5 Mtr. per substation) | 7130641396 | Mtr | 190 | 63 | 11970
19 | G.I. Wire 8 SWG | 7130870043 | Kg | 55.094 | 180 | 9916.92
20 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1048 | 45 | 47160
21 | 11 kV Top clamp | 7130810679 | No | 294 | 45 | 13230
22 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 157 | 135 | 21195 | Earlier- 11 kV Pin Insulator
23 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 45 | 4500
24 | M.S. Nuts and Bolts |  | Kg |  | 250
| 16x40 mm | 7130620609 | Kg | 64 | 40 | 2560
| 16x65 mm | 7130620614 | Kg | 63 | 80 | 5040
| 16x90 mm | 7130620619 | Kg | 63 | 10 | 630
| 16x140 mm | 7130620625 | Kg | 62 | 40 | 2480
| 16x160 mm | 7130620627 | Kg | 62 | 40 | 2480
| 16X200 mm | 7130620631 | Kg | 62 | 40 | 2480
25 | Concreting of stay @ 0.2 Cmt/stay |  | Cmt
| (I) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 1248 | 6689.28
26 | I - Bolt 16 mm | 7130860017 | No | 100 | 21 | 2100
27 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.281 | 900 | 18252.9
28 | SUB TOTAL-1 |  |  |  |  | 999137.04
29 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 89922.3336
30 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 138.8677 | 8 | 1110.9416
31 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 6 | 17810.7659
32 | Labour charges [as per Sch. No.- DL-11] |  |  |  |  | 104946.12
33 | Transportation charges |  |  |  |  | 7506.2105
34 | SUB TOTAL-2 |  |  |  |  | 1220433.4116
35 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 109905.0744
36 | Total cost per Km for non-guaranteed works |  |  |  |  | 1330338.486
37 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 1330338
Note: All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-9
COST SCHEDULE D-9
HVDS SYSTEM OF 63 kVA PARENT DTR TAKING 2 KM. LT TO BE CONVERTED
2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 25 kVA 11/0.4 kV Transformer 4 STAR | 7132210008 | No | 54268 | 1 | 54268
2 | 16 kVA 11/0.4 kV conventional Transformer (4 STAR Aluminium Wound) | 7132210007 | No | 44836 | 2 | 89672
3 | 10 kVA 11/0.4 kV SINGLE PHASE Transformer | 7132210078 | No | 36194 | 3 | 108582
4 | 140 Kg 8 Mtr. Long PCC Pole (for mid span) | 7130800012 | No | 1654 | 6 | 9924
5 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 25 | 9675
| (ii) Stay Wire 7/10 SWG (5.5 kg/stay) | 7130860077 | Kg | 61.6 | 137.5 | 8470
| (iii) Stay Clamp for 140 kg PCC Pole | 7130810026 | No | 142 | 25 | 3550
6 | Transformer mounting arrangement DC cross arm 100x50x6 mm. 2.7 mtr long 8' Centre | 7130850201 | Set | 4547 | 5 | 22735
7 | DC cross arm 100x50x6 mm 8 ' Centre 2.7 mtr long | 7130850201 | Set | 4547 | 5 | 22735
8 | DO Mounting Channel | 7130810509 | Set | 3322 | 5 | 16610
9 | 11 kV Single Pole cut point channel | 7130810681 | No | 3227 | 10 | 32270
10 | 11 kV Strain Hardware set | 7130820241 | Set | 123 | 36 | 4428
11 | 11 kV Polymer Disc Insulator | 7130820010 | No | 140 | 36 | 5040 | Earlier- 11 kV Disc Insulator
12 | 11 kV Polymer Lightning Arrestor | 7130840029 | No | 425 | 15 | 6375 | Earlier- 11 kV L.A. set
13 | 11 kV D.O. Set | 7131930412 | No | 1199 | 15 | 17985
14 | Protection cum metering box with 40 Amp. MCCB & 4 No. 3 phase meter for 25 kVA X-mer |  | No | 16000 | 2 | 32000
15 | Protection cum metering box with 25 Amp. MCCB & 3 No. 3 phase meter for 16 kVA X-mer |  | No | 13000 | 3 | 39000
16 | 35 sqmm single core XLPE cable | 7130310021 | Mtr | 39.632 | 100 | 3963.2
17 | XLPE insulated 4 core 10 sqmm. armoured cable | 7130310044 | Mtr | 94.953 | 1300 | 123438.9
18 | G.I. Pipe 40 mm (5 Mtr. per Sub-station) | 7130641396 | Mtr | 190 | 45 | 8550
19 | G.I. Wire 8 SWG | 7130870043 | Kg | 55.094 | 130 | 7162.22
20 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 1048 | 45 | 47160
21 | 11 kV Top clamp | 7130810679 | No | 294 | 45 | 13230
22 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 157 | 135 | 21195 | Earlier- 11 kV Pin Insulator
23 | Earthing Set (Coil earth as per Drawing No- G/004 | 7130870013 | No | 100 | 45 | 4500
24 | M.S. Nuts and Bolts |  | Kg |  | 190
| 16x40 mm | 7130620609 | Kg | 64 | 30 | 1920
| 16x65 mm | 7130620614 | Kg | 63 | 60 | 3780
| 16x90 mm | 7130620619 | Kg | 63 | 10 | 630
| 16x140 mm | 7130620625 | Kg | 62 | 30 | 1860
| 16x160 mm | 7130620627 | Kg | 62 | 30 | 1860
| 16X200 mm | 7130620631 | Kg | 62 | 30 | 1860
25 | Concreting of stay @ 0.2 Cmt/stay |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/cmt | 7130200401 | Kg | 5.36 | 1040 | 5574.4
26 | I - Bolt 16 mm | 7130860017 | No | 100 | 10 | 1000
27 | ACSR Weasel conductor for Reconductoring | 7130830055 | Mtr | 20.281 | 600 | 12168.6
28 | SUB TOTAL-1 |  |  |  |  | 743171.32
29 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 66885.4188
30 | Back filling of pole pit with boulders @ 0.25 Cmt. |  | No | 138.8677 | 6 | 833.2062
31 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 5 | 14842.3049
32 | Labour charges [as per Sch. No.- DL-12] |  |  |  |  | 79276.47
33 | Transportation charges |  |  |  |  | 5629.6605
34 | SUB TOTAL-2 |  |  |  |  | 910638.3805
35 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 81748.8452
36 | Total cost per Km for non-guaranteed works |  |  |  |  | 992387.2257
37 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 992387
Note:- | All the rates are considering with price variation clause. Actual returnable material schedule may be prepared separately.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-10
COST SCHEDULE D-10
CONVERSION OF 1 KM LT LINE INTO 11 kV LINE
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Poles (for where ever required ) | 7130800012 | No | 1 | 1654 | 1654
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 17 | 1048 | 17816
3 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 17 | 294 | 4998
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 17 | 100 | 1700
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 51 | 157 | 8007 | Earlier- 11 kV Pin Insulator
6 | Jointing sleeves suitable for Weasel/ Rabbit conductor | 7130830854 | No | 6 | 26 | 156
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 130 | 390
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 290 | 870
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 17 | 66.528 | 1130.976
10 | Danger Board | 7130880041 | No | 17 | 74 | 1258
11 | Binding wires & tape | 7130830006 | Kg | 5 | 139 | 695
12 | Nuts and bolts
| 16x90 mm | 7130620619 | Kg | 2 | 63 | 126
| 16x160 mm | 7130620627 | Kg | 17 | 62 | 1054
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2485 | 2485
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 55.094 | 1928.29
| (iii) Stay clamp (Pair) H.T. | 7130810026 | No | 2 | 265 | 530
| (iv) Stay wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 61.6 | 677.6
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 387 | 774
| (vi) I - Bolt big size. | 7130620013 | No | 4 | 118 | 472
14 | Concreting of stay @ 0.2 Cmt per stay and 0.05 Cmt base pad per pole |  | Cmt
| Cement @ 208 Kg per Cmt | 7130200401 | Kg | 104 | 5.36 | 557.44
15 | SUB TOTAL-1 |  |  |  |  | 47279.306
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 4255.1375
17 | Back filling of poles with bolders @ of 0.3 Cmt per pole |  | No | 1 | 188.9746 | 188.9746
18 | Service in lieu of concreting metal and sand |  | Cmt | 0.5 | 2968.461 | 1484.2305
19 | Labour charges as per Schedule No. DL-3 (E-1) |  |  |  |  | 23211.31
20 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 3659.2839
21 | SUB TOTAL-2 |  |  |  |  | 80078.2426
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 5200.7237
23 | Cost per Km. for Non guaranteed works |  |  |  |  | 85278.9662
24 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 85279
Note:- | (i) Three wire LT line will be utilized for converting into 11 kV line.
(ii) For replacement of deteriorated conductor of LT line suitable provision should be made while preparing the estimates
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-11
COST SCHEDULE D-11
2015-16
LT LINE CONVERSION USING RABBIT CONDUCTOR MAXIMUM SPAN OF 45 MTRS.
S. No. | PARTICULARS | New Bin code | Unit | Rate | 1 Phase 2 Wire to 1 Phase 3 Wire Conversion |  | 1 Phase 2 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 4 Wire Conversion |  | 1 Phase 3 Wire to 3 Phase 5 Wire Conversion
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | LT Three Pin cross arm | 7130810413 | No | 618 | 24 | 14832
2 | LT Four Pin cross arm | 7130810441 | No | 736 |  |  | 24 | 17664 | 24 | 17664
3 | LT Five Pin cross arm | 7130810461 | No | 854 | [6 empty] | 24 | 20496
4 | LT Shackle Insulator (90x75 mm) | 7130820106 | No | 10 | 24 | 240 | 48 | 480 | 24 | 240 | 48 | 480
5 | Hardware for Shackle Insulator | 7130820216 | No | 34 | 8 | 272 | 16 | 544 | 8 | 272 | 16 | 544
6 | ACSR RABBIT Conductor including 3% Sag | 7130830057 | Mtr | 33.544 | 1030 | 34550.32 | 2060 | 69100.64 | 1030 | 34550.32 | 2060 | 69100.64
7 | Split insulator for guarding | 7130820018 | Pair | 3 | 40 | 120 | 40 | 120 | 40 | 120 | 40 | 120
8 | M.S. Nuts & bolts
| 12x100 mm | 7130620573 | Kg | 64 | 4 | 256 | 8 | 512 | 4 | 256 | 8 | 512
| 16x40 mm | 7130620609 | Kg | 64 | 4 | 256 | 6 | 384 | 4 | 256 | 6 | 384
| 16x140 mm | 7130620625 | Kg | 62 | 10 | 620 | 10 | 620 | 10 | 620 | 10 | 620
| 16x65 mm | 7130620614 | Kg | 63 | 6 | 378 | 6 | 378 | 6 | 378 | 6 | 378
9 | Red Oxide Paint | 7130211158 | Ltr | 130 | 1 | 130 | 1 | 130 | 1 | 130 | 1 | 130
10 | Aluminium Paint | 7130210809 | Ltr | 290 | 1 | 290 | 1 | 290 | 1 | 290 | 1 | 290
11 | G.I. Wire 4 mm for guarding | 7130870043 | Kg | 55.094 | 6 | 330.564 | 7.5 | 413.205 | 7.5 | 413.205 | 7.5 | 413.205
12 | Clamp for R.S. Joist or PCC 140 Kg./8 mtr long | 7130810216 | No | 282 | 20 | 5640 | 20 | 5640 | 20 | 5640 | 20 | 5640
13 | SUB TOTAL-1 |  |  |  |  | 57914.884 |  | 96275.845 |  | 60829.525 |  | 99107.845
14 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 5212.3396 |  | 8664.826 |  | 5474.6573 |  | 8919.7061
15 | Labour Charges as per DL-4. |  |  |  |  | 9429.97 |  | 13688.93 |  | 9429.97 |  | 13688.93
16 | Transportation Charges ` |  |  |  |  | 2927.4272 |  | 3476.3197 |  | 2927.4272 |  | 3476.3197
17 | SUB TOTAL-2 |  |  |  |  | 75484.6207 |  | 122105.9208 |  | 78661.5794 |  | 125192.8008
18 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 6370.6372 |  | 10590.343 |  | 6691.2478 |  | 10901.863
19 | Grand Total |  |  |  |  | 81855.258 |  | 132696.2637 |  | 85352.8272 |  | 136094.6637
20 | Total (rounding off) |  |  |  |  | 81855 |  | 132696 |  | 85353 |  | 136095

## D-12
COST SCHEDULE D-12 ( E-2)
2015-16
CONVERSION OF 1 KM 1 PHASE 3 WIRE LT LINE INTO 11 kV LINE
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required ) | 7130800012 | No | 1 | 1654 | 1654
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1048 | 23056
3 | 11 kV Top clamp Angle type with cleat. | 7130810679 | No | 22 | 294 | 6468
4 | Earthing set (coil earth as per Drawing No.G/007) | 7130870013 | No | 22 | 100 | 2200
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 157 | 10362 | Earlier- 11 kV Pin Insulator
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 26 | 156
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 130 | 390
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 290 | 870
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 66.528 | 1463.616
10 | Danger Board | 7130880041 | No | 22 | 74 | 1628
11 | Binding wire & tape | 7130830006 | Kg | 5 | 139 | 695
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | Kg | 2 | 63 | 126
| 16x160 mm | 7130620627 | Kg | 17 | 62 | 1054
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 12 | 2485 | 29820
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 55.094 | 24296.454
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 265 | 530
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 61.6 | 677.6
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 387 | 774
| (vi) I- Bolt big size. | 7130620013 | No. | 4 | 118 | 472
14 | Concreting of stay @ 0.2 Cmt per stay and @ 0.05 Cmt base pad per pole |  | Cmt
| Cement @ 208 Kg per Cmt. | 7130200401 | Kg | 104 | 5.36 | 557.44
15 | PVC Insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 15.99 | 33642.96
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 13.002 | 13392.06
17 | SUB TOTAL-1 |  |  |  |  | 154285.13
18 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 13885.6617
19 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 2 | 188.9746 | 377.9492
20 | Service in lieu of concreting metal and sand |  | Cmt. | 0.5 | 2968.461 | 1484.2305
21 | Labour charges as per Schedule No. DL-5 ( E-2) |  |  |  |  | 34020.42
22 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 3659.2839
23 | SUB TOTAL-2 |  |  |  |  | 207712.6754
24 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 16971.3643
25 | Cost per Km. for Non guaranteed works |  |  |  |  | 224684.0397
26 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 224684
Note:- | (1) In 1 Phase 3 Wire L.T. three wire conductor will be reutilised.
(2) In Case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-13
COST SCHEDULE D-13 (E-3)
CONVERSION OF 1 kM 3 PHASE 5 WIRE LT LINE INTO 11 kV LINE
2015-16
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg 8.0 meter long PCC Pole (for where ever required) | 7130800012 | No | 1 | 1654 | 1654
2 | 11 kV 'V' Cross arm with clamp | 7130810495 | No | 22 | 1048 | 23056
3 | 11 kV Top Clamp Angle type with cleat. | 7130810679 | No | 22 | 294 | 6468
4 | Earthing set (coil earth as per Drawing No.G/007 | 7130870013 | No | 22 | 100 | 2200
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 66 | 157 | 10362 | Earlier- 11 kV Pin Insulator
6 | Jointing sleeves suitable for weasel / rabbit conductor | 7130830854 | No | 6 | 26 | 156
7 | Red Oxide Paint | 7130211158 | Ltr | 3 | 130 | 390
8 | Aluminium Paint | 7130210809 | Ltr | 3 | 290 | 870
9 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 22 | 66.528 | 1463.616
10 | Danger Board | 7130880041 | No | 22 | 74 | 1628
11 | Binding wire & tape | 7130830006 | Kg | 5 | 139 | 695
12 | Nuts and Bolts
| 16x90 mm | 7130620619 | kg | 2 | 63 | 126
| 16x160 mm | 7130620627 | kg | 17 | 62 | 1054
13 | Guarding
| (i) 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 23 | 2485 | 57155
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 441 | 55.094 | 24296.454
| (iii) Stay Clamp (Pair) H.T. | 7130810026 | No | 2 | 265 | 530
| (iv) Stay Wire 7/10 SWG @ 5.5 kg/stay | 7130860077 | Kg | 11 | 61.6 | 677.6
| (v) Stay set 16 mm. | 7130860032 | No | 2 | 387 | 774
| (vi) I-Bolt big size. | 7130620013 | No. | 4 | 118 | 472
14 | Concreting of stay @ 0.2 Cmt. per stay and 0.05 Cmt. base pad per pole |  | Cmt.
| Cement @ 208 Kg per Cmt. | 7130200401 | Kg | 104 | 5.36 | 557.44
15 | PVC insulated cable 16 sqmm 1 core unarmoured | 7130311008 | Mtr. | 2104 | 15.99 | 33642.96
16 | ACSR Conductor 20 sqmm. Al. Eq. for neutral | 7130830053 | Mtr | 1030 | 13.002 | 13392.06
17 | SUB TOTAL-1 |  |  |  |  | 181620.13
18 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 16345.8117
19 | Back filling of pole with boulders @ 0.3 Cmt. per pole. |  | No. | 2 | 188.9746 | 377.9492
20 | Service in lieu of concreting metal and sand |  | Cmt | 0.5 | 2968.461 | 1484.2305
21 | Labour charges as per Schedule No. DL-6 (E-3) |  |  |  |  | 35526.38
22 | Transport charges upto 50 Kms. Average lead from Area Store to construction camping site transport |  |  |  |  | 3659.2839
23 | SUB TOTAL-2 |  |  |  |  | 239013.7854
24 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 19978.2143
25 | Cost per Km. for Non guaranteed works |  |  |  |  | 258991.9997
26 | Cost per Km. for Non guaranteed works (Rounded off) |  |  |  |  | 258992
Note:- | (1) In 3 Phase 5 Wire LT system, 5th conductor i.e. neutral conductor and 4th conductor will be returned to Area Stores and depreciated value of neutral conductor will be accounted for at the time of estimate framing. L.T. Phase conductor will be reutilised.
(2) In case of replacement of Old conductor, new conductor may be incorporated in the estimate and depreciated value will be accounted for in the estimate.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## D-14
COST SCHEDULE -- D-14
DISTRIBUTION BOX ON EXISTING LT LINES FOR SERVICE CONNECTIONS
2015-16
S. No. | DESCRIPTION | Bin Code No | UNIT | Rate per Distribution Box | Incidental Charges (9%) | Labour Charges per Distribution Box | Cost per Distribution Box | Cost per Distribution Box Round Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Single phase Distribution box for 9 connections | 7131950010 | Nos. | 1147 | 103.23 | 100 | 1350.23 | 1350
2 | Three phase Distribution box for 5 connections | 7131950012 | Nos. | 1355 | 121.95 | 100 | 1576.95 | 1577
| Incidental Charges @ 9% : - |  |  | 9%

## D-15
COST SCHEDULE -- D-15
1 KM OF 1 PHASE 2 WIRE LINE ON 140 KG. PCC POLE 8 MTR. LONG USING AB XLPE CABLE FOR RURAL AREAS WITH MAXIMUM SPAN 50 MTRS.
2015-16
S. No. | PARTICULARS | New Bin Code | Unit | Rate | 140 Kg, 8.0 Mtr. long PCC support Using 1100 V grade AB Cable 1x16 + 1x25 sqmm.
[5 empty] | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC support | 7130800012 | No | 1654 | 20 | 33080
2 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797533 | No | 435 | 20 | 8700
3(i) | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | 7130390003 | No | 80 | 24 | 1920 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-for street light
(ii) | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | 7130390004 | No | 104 | 10 | 1040 | Earlier- Piercing connector suitable for 25/16 Sq.mm-50/35 Sqmm AB Cable-Distribution Box (1 No. per 1 phase DB)
(iii) | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | 7130390005 | No | 145 | 6 | 870 | Earlier- Piercing connector suitable for AB Cable to AB Cable Tee connections.
4 | Distribution box 1 phase 9 connectors along with 2 Nos. Steel Strap & Buckles | 7131950010 | Each | 1147 | 20 | 22940
5 | Universal distribution connector | 7130390006 | No | 149 | 41 | 6109
6 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | 7130797532 | No | 599 | 44 | 26356
7 | LT 1 phase 2 Wire AB XLPE Cable 1x16 + 1x25 sqmm. (6% sag) |  | Mtr | 40.129 | 1100 | 44141.9
8 | (i) Stay Set 16 mm (Complete) | 7130860032 | No | 387 | 12 | 4644
| (ii) Stay Wire 7/10 SWG & 6 Kg/Stay | 7130860077 | Kg | 61.6 | 72 | 4435.2
| (iii) Stay Clamp | 7130810026 | No | 142 | 12 | 1704
9 | Concreting of stay & pole @ 0.2 Cmt/stay and @ 0.3 Cmt/pole for RSJ, @ 0.5 Cmt/pole for H-Beam pole i.e. 8.4 Cmt for RSJ & 12.4 Cmt for H-Beam pole |  | Cmt 1:3:6
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5.36 | 707 | 3789.52
10 | M.S. Nuts and Bolts |  | Kg |  | 30
| 12x100 mm | 7130620573 | Kg | 64 | 2 | 128
| 16x40 mm | 7130620609 | Kg | 64 | 14 | 896
| 16x65 mm | 7130620614 | Kg | 63 | 14 | 882
11 | Earthing Set (Coil earth as per Drawing No- G/004) | 7130870013 | No | 100 | 6 | 600
12 | Red Oxide Paint | 7130211158 | Ltr | 130 | 3 | 390
13 | Aluminium Paint | 7130210809 | Ltr | 290 | 3 | 870
14 | Service Ring | 7130810102 | No | 349 | 30 | 10470
15 | PVC insulated single core 16 sq.mm. cable @ 3 mtr. per 1 phase box | 7130311008 | Mtr | 15.99 | 60 | 959.4
16 | Straight through joints | 7130390007 | No | 172 | 10 | 1720
17 | End cap for 50/70 Sq.mm | 7130390019 | No | 28 | 10 | 280
18 | Barbed wire [(@ 2 kg per pole] | 7130610206 | Kg | 66.528 | 70 | 4656.96
19 | SUB TOTAL-1 |  |  |  |  | 181581.98
20 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 16342.3782
21 | Back filling of pole pit with boulder @ 0.3 Cmt./pole |  | No. | 187.2721 | 20 | 3745.4427
22 | Service in lieu of concreting metal & sand only |  | Cmt | 2968.461 | 3.4 | 10092.7673
23 | Labour charges as per schedule DL-8 |  |  |  |  | 35903.79
24 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 9681.2378
25 | SUB TOTAL-2 |  |  |  |  | 257347.596
26 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 19974.0178
27 | Total cost per Km for non-guaranteed works |  |  |  |  | 277321.6138
28 | Total cost per Km for non-guaranteed works (R/Off) |  |  |  |  | 277322
Note:- All the rates are with considering price variation clause.

## E-1
COST SCHEDULE -- E-1
METERING OF 11/0.4 kV DISTRIBUTION TRANSFORMER (TO BE SUPPLEMENTED WITH COST SCHEDULE C-7 (A1, A2, B1, B2, C1, C2)
2015-16
S. No. | PARTICULARS | Bin Code No | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1(a) | Poly phase static energy meter 10-60 Amp. with meter box | 7131300046 | No | 1 | 2326 | --
1(b) | CT operated electronic static meter 100/5 Amp. | 7131310997 | No | 1 | 2487 | 2487 | 1 | 2487 | 2487 | 1 | 2487 | 2487 | 1 | 2487 | 2487
2 | LT CT :-
| (i) 100/5 Amp. | 7132230016 | No | 4 | 335 | 1340 | 4 | 335 | 1340 | -- | -- | -- | -- | -- | --
| (ii) 200/5 Amp. | 7132230019 | No | -- | -- | -- | -- | -- | -- | 4 | 335 | 1340 | -- | -- | --
| (iii) 300/5 Amp. | 7132230021 | No | -- | -- | -- | -- | -- | -- | -- | -- | -- | 4 | 268 | 1072
3 | Meter Box (G.I. Plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2437 | 2437 | 1 | 2437 | 2437 | 1 | 2437 | 2437 | 1 | 2437 | 2437
4 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 67.671 | 812.052 | 12 | 67.671 | 812.052 | 12 | 67.671 | 812.052 | 12 | 67.671 | 812.052
5 | SUB TOTAL-1 |  |  |  |  | 7076.052 |  |  | 7076.052 |  |  | 7076.052 |  |  | 6808.052
6 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 636.8447 |  | 0.09 | 636.8447 |  | 0.09 | 636.8447 |  | 0.09 | 612.7247
7 | Labour & Transportation charges |  |  |  |  | 2213.8668 |  |  | 2213.8668 |  |  | 2213.8668 |  |  | 2213.8668
8 | SUB TOTAL-2 |  |  |  |  | 9926.7635 |  |  | 9926.7635 |  |  | 9926.7635 |  |  | 9634.6435
9 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 778.3657 |  | 0.11 | 778.3657 |  | 0.11 | 778.3657 |  | 0.11 | 748.8857
10 | Cost of Metering for non-guaranteed works |  |  |  |  | 10705.1292 |  |  | 10705.1292 |  |  | 10705.1292 |  |  | 10383.5292
11 | Cost of Metering for non-guaranteed works (Rounded off). |  |  |  |  | 10705 |  |  | 10705 |  |  | 10705 |  |  | 10384
Note:- All the rates are with considering price variation clause.
38

## E-2
COST SCHEDULE -- E-2
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| SINGLE PHASE CONNECTION |  |  |  |  | 2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Single Phase Static Meter 5-30 Amps. Pilfer Proof with transparent polycarbonate meter box | 7131300500 | No | 1 | 975 | 975 | 975 | 975
2 | Armoured Service Cable - Single Phase, 2 core- 6 sq mm |  | Mtr | 30 | 36 | 1080
3 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 27 | 810
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No | 2 | 9 | 18 | 9 | 18
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No | 2 | 30 | 60 | 30 | 60
6 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | No | 1 | 131 | 131 | 131 | 131
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 15 | 15 | 15 | 15
8 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 35 | 35 | 35 | 35
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 |  |  |  |  | 2344 |  | 2074
11 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 210.96 | 0.09 | 186.66
12 | Labour Charges |  | Per Installation |  |  | 175.5837 |  | 175.5837
13 | Cost for meter replacement of a Single Phase Consumer |  |  |  |  | 2730.5437 |  | 2436.2437
14 | Cost for meter replacement of a Single Phase Consumer (Round off) |  |  |  |  | 2731 |  | 2436

## E-3
COST SCHEDULE -- E-3
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION |  |  |  |  | 2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT 3 phase electronic energy meter 10-60 Amps. with poly carbonate meter box | 7131300046 | No. | 1 | 2326 | 2326 | 2326 | 2326
2 | Armoured Service Cable - Three Phase, 4 core-10 sq mm |  | Mtr | 30 | 62 | 1860
3 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 55 | 1650
4 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 9 | 18 | 9 | 18
5 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 30 | 60 | 30 | 60
6 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 274 | 274 | 274 | 274
7 | PVC Insulation Tape | 7132476007 | Roll | 1 | 15 | 15 | 15 | 15 | Unit earlier-Lot
8 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 35 | 35 | 35 | 35
9 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
10 | SUB TOTAL-1 |  |  |  |  | 4618 |  | 4408
11 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 415.62 | 0.09 | 396.72
12 | Labour Charges |  | Per Installation |  |  | 280.934 |  | 280.934
13 | Cost for meter replacement of a Three Phase Consumer |  |  |  |  | 5314.554 |  | 5085.654
14 | Cost for meter replacement of a Three Phase Consumer (Round Off) |  |  |  |  | 5315 |  | 5086
| No of Consumers for Meter Replacement |  |  | 100
| Total Cost |  |  |  |  | 531455.3997 |  | 508565.3997
| Total Cost Round Off |  |  |  |  | 531455 |  | 508565

## E-4
COST SCHEDULE -- E-4
METER MODERNISATION : REPLACING THE EXISTING METERS WITH ELECTRONIC METERS WHICH ARE HIGHLY CAPABLE OF IMPROVING BILLING EFFICIENCY ALONGWITH SHIFTING OF METER OUTSIDE THE PREMISES.
| THREE PHASE CONNECTION CT- OPERATED METERS |  |  |  |  | 2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Qty | Rate | Amount
1 | CT Operated Electronic Static Meters 100/5 Amp. with data storage | 7131310997 | No. | 1 | 2487 | 2487
2 | PVC Insulation Tape | 7132476007 | Roll | 1 | 15 | 15 | Unit earlier-Lot
3 | Misc Items , e.g., Screw, cut-outs |  | Lot | 1 | 40 | 40
4 | M-Seal |  | Lot | 1 | 30 | 30
5 | SUB TOTAL-1 |  |  |  |  | 2572
6 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 231.48
7 | Labour Charges |  | Per Installation |  |  | 280.934
8 | Cost for meter replacement of Three Phase Consumer CT Operated Meters |  |  |  |  | 3084.414
9 | Cost for meter replacement of 3- Phase Consumer CT Operated Meters (Round Off) |  |  |  |  | 3084

## E-5
COST SCHEDULE -- E-5
METER SHIFTING OF SINGLE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| SINGLE PHASE CONNECTION | [5 empty] | 2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Single Phase, 2 core- 6 sq. mm. |  | Mtr | 30 | 36 | 1080
2 | Unarmoured Service Cable - Single Phase, 2 core- 6 sq mm | 7130310039 | Mtr | 30 |  |  | 27 | 810
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 9 | 18 | 9 | 18
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 30 | 60 | 30 | 60
5 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | 7132406022 | Nos | 1 | 131 | 131 | 131 | 131
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 15 | 15 | 15 | 15 | Unit earlier-Lot
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 35 | 35 | 35 | 35
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 |  |  |  |  | 1369 |  | 1099
10 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 123.21 | 0.09 | 98.91
11 | Labour Charges |  | Per Installation |  |  | 175.5837 |  | 175.5837
12 | Cost for meter shifting of a Single Phase Consumer |  |  |  |  | 1667.7937 |  | 1373.4937
13 | Cost for meter shifting of a Single Phase Consumer (Round Off) |  |  |  |  | 1668 |  | 1373

## E-6
COST SCHEDULE -- E-6
METER SHIFTING OF THREE PHASE CONSUMER TO OUTSIDE OF PREMISES WITH NEW SERVICE CABLE
| THREE PHASE CONNECTION | [5 empty] | 2015-16
S. No. | PARTICULARS | Bin Code No. | Unit | Qty. | Armoured service cable |  | Unarmoured service cable
[5 empty] | Rate | Amount | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Armoured Service Cable - Three Phase , 4 core-10 sq mm |  | Mtr | 30 | 62 | 1860
2 | Unarmoured Service Cable - Three Phase, 4 core-10 sq mm | 7130310040 | Mtr | 30 |  |  | 55 | 1650
3 | LT Shackle Insulator 65x50 mm | 7130820101 | No. | 2 | 9 | 18 | 9 | 18
4 | H/W for 65x50 mm Shackle Insulator | 7130820206 | No. | 2 | 30 | 60 | 30 | 60
5 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | 7132455002 | Nos | 1 | 274 | 274 | 274 | 274
6 | PVC Insulation Tape | 7132476007 | Roll | 1 | 15 | 15 | 15 | 15 | Unit earlier-Lot
7 | Misc Items , e.g., Screw, cut outs |  | Lot | 1 | 35 | 35 | 35 | 35
8 | M-Seal |  | Lot | 1 | 30 | 30 | 30 | 30
9 | SUB TOTAL-1 |  |  |  |  | 2292 |  | 2082
10 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 206.28 | 0.09 | 187.38
11 | Labour Charges |  | Per Installation |  |  | 280.934 |  | 280.934
12 | Cost for meter shifting of a Three Phase Consumer |  |  |  |  | 2779.214 |  | 2550.314
13 | Cost for meter shifting of a Three Phase Consumer (Round Off) |  |  |  |  | 2779 |  | 2550