## COMPARATIVE
COMPARATIVE STATEMENT OF RATES FROM YEAR 2025-26 to 2026-27
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2025-26 | 2026-27 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
PART-I, 33 kV LINES AND D.P. STRUCTURES
(A) |  | 33 kV line on PCC Pole / H-Beam poles with Raccoon conductor.
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-1(i) | Per Km | 547539 | 579712 | 5.8759
| ii | On H-Beam 152 x 152 mm 37.1 Kg/ Mtr 13 Mtr long | A-1(ii) | Per Km | 864995 | 872437 | 0.86035
| iii | On 365 Kg 11 Mtrs long PCC poles | A-1(iii) | Per Km | 610779 | 642951 | 5.2674
(B) |  | 33 kV Four Pole structure on PCC / H-Beam Pole | A-2 (A)
| i | On 280 Kg 9.1 Mtrs long PCC poles | A-2 (A) (i) | Each | 355208 | 350001 | -1.4659
| ii | H-Beam Pole | A-2 (A) (ii) | Each | 479408 | 464277 | -3.1562
(C) |  | 33 kV DP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-2 (B)(i) | Each | 75922 | 74994 | -1.2223
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-2 (B)(ii) | Each | 136800 | 130916 | -4.3012
| iii | On 365 Kg 11 Mtrs long PCC poles | A-2 (B)(iii) | Each | 84776 | 83848 | -1.0946
(D) |  | 33 kV line on PCC Pole / H-Beam Pole with Dog conductor.
| i | On 280 Kg, 9.1 Mtrs long PCC poles | A-3(i) | Per Km | 658010 | 702262 | 6.7251
| ii | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3(ii) | Per Km | 975468 | 994989 | 2.0012
| iii | On 365 Kg 11 Mtrs long PCC poles | A-3(iii) | Per Km | 721145 | 765397 | 6.1364
(E) |  | Augmentation of 1 km. of 33 kV line from Raccoon to Dog conductor. | A-3 (A) | Per Km | 453741 | 500720 | 10.3537
(F) |  | Additional (Mid Span) Pole for 33 kV Line | A-3 (B)
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-3 (B)(i) | Per No. | 49459 | 46974 | -5.0244
(G) |  | 33 kV line on H-Beam supports suspension type with Panther Conductor (Maximum span of 50 Mtrs) | A-4
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-4 (i) | Per Km | 2462025 | 2534269 | 2.9343
(H) |  | 33 kV DP Structure on H-Beam supports with Panther Conductor | A-5
| i | On H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-5 (i) | Each | 156415 | 150334 | -3.8877
(I) |  | 33 kV Under ground cable crossing under existing Railway track / Road for 60 Mtr long Corridor / route length of G.I.Pipe/HDPE pipe under 2.5 M. deep for ground level single feeder line | A-6 | 60 Mtr
| i | Using HDD Technique for Railway works with 3 core U/G XLPE 400 sqmm Cable | A-6(i) | 60 Mtr | 2354729 | 2416578 | 2.6266
| ii | Using HDD Technique for Road crossing works with 3 core U/G XLPE 400 sqmm Cable | A-6(ii) | 60 Mtr | 2158842 | 2227400 | 3.1757
(J) |  | Last span cabling of 33 kV H.T. Connection
|  | Using H-Beam 152x152 mm, 37.1Kg/mtr 13 Mtrs long supports. | A-7
| i | With 3x185 sq.mm AB XLPE Cable | A-7(i) | 50 Mtr | 264497 | 271325 | 2.5815
| ii | With 3x240 sq.mm AB XLPE Cable | A-7(ii) | 50 Mtr | 302440 | 311949 | 3.1441
(K) |  | 33 kV MEDP Structure on PCC Pole / H-Beam Pole
| i | 280 Kg 9.1 Mtrs long PCC poles | A-8 (i) | Each | 122372 | 122759 | 0.31625
| ii | 37.1 Kg /Mtrs 13 Mtrs long H-Beam supports | A-8 (ii) | Each | 183160 | 178593 | -2.4934
(L) |  | Last span cabling of 33 kV line using Covered Conductor of size
| i | 70 sq.mm (207 Amp) | A-9 (i) | 50 Mtr | 200778 | 202729 | 0.97172
| ii | 99 sq.mm (258 Amp) | A-9 (ii) | 50 Mtr | 209475 | 211891 | 1.1534
(M) |  | Schedule for 33 kV Underground Cable crossing under Railway Track / Road for 60 Mtr. Long Corridor / Route Length of G.I.Pipe/HDPE Pipe, under 2.5 Mtr. Deep from Ground Level Single Feeder Line Using Open Trench Method. | A-10
| a | For Railway works
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 1768072 | 1820168 | 2.9465
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1989130 | 2051273 | 3.1241
| b | For Road crossing works
| i | With 3 core U/G XLPE 240 sqmm Cable | A-10(i) | 60 Mtr | 1572667 | 1631504 | 3.7412
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-10(ii) | 60 Mtr | 1793724 | 1862609 | 3.8403
(N) |  | Schedule for laying of 1 km. 33 kV Cable Direct in Ground Single Cable Line using Open Trench Method. | A-11
| i | With 3 core U/G XLPE 240 sqmm Cable | A-11(i) | Per Km | 6366616 | 6721372 | 5.5721
| ii | With 3 core U/G XLPE 400 sqmm Cable | A-11(ii) | Per Km | 6885607 | 7268985 | 5.5678
(O) |  | Schedule for laying of 1 km. 33 kv overhead AB cable line suitable to 95 / 150 Sqmm. on H - Beam pole with Average span 25 mtrs. | A-12 (A)
| i | Using 33 kV 3 core A.B. XLPE Cable of size 95 sqmm | A-12(A)(i) | Per Km | 3731148 | 3795014 | 1.7117
| ii | Using 33 kV 3 core A.B. XLPE Cable of size 150 sqmm | A-12(A)(ii) | Per Km | 4258538 | 4356824 | 2.308
(P) |  | Schedule for laying of 1 km. 33 kv overhead AB cable line on H - Beam pole with Average span 20 mtrs suitable above 150 Sqmm. | A-12 (B)
| i | Using 33 kV 3 core A.B. XLPE Cable of size 185 sqmm | A-12(B)(i) | Per Km | 4912209 | 5013738 | 2.0669
| ii | Using 33 kV 3 core A.B. XLPE Cable of size 240 sqmm | A-12(B)(ii) | Per Km | 5495219 | 5650734 | 2.83

## SOR RATE 2026-27
RATE OF STOCK MATERIALS IN SoR OF 2026-27
RATE OF ALL MATERIALS ARE INCLUSIVE OF G.S.T. UNLESS MENTIONED SPECIFICALLY IN REMARKS COLUMN
Material Code | Description | Unit | Unit rate for 2026-27 | SAP DESCRIPTION | REMARKS
7130200201 | 1:1.5:3 Ratio | Cmt | 4073 |  |  | Rate are inclusive of all T&P and labour charges
7130200001 | 1:2:4 Ratio | Cmt | 3552 |  |  | Rate are inclusive of all T&P and labour charges
7130200202 | 1:3:6 Ratio | Cmt | 2970 |  |  | Rate are inclusive of all T&P and labour charges
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 207.78 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 354 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Each | 34.5 |  |  | Rate are inclusive of all T&P and labour charges
7130210809 | Aluminium Paint | Ltr. | 409.72 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 313.68
7130211158 | Red Oxide Paint | Ltr. | 183.37 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 345952.9 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5 | ISI MARK
7130310007 | 70 Sqmm. | Km. | 84041.77 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V | ISI MARK
7130310008 | 120 Sqmm. | Km. | 153470.73 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100 | ISI MARK
7130310020 | 33 kV 3 CORE XLPE UG CABLE 3x400 Sq.mm. | km | 3202949.27 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 48196.36 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V | ISI MARK
7130310022 | 50 Sqmm. | Km. | 61736.86 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V | ISI MARK
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 117441.13 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM | ISI MARK
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 151505.38 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM | ISI MARK
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 181440.54 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM | ISI MARK
7130310038 | 2.5 Sqmm. | Per Mtr. | 10.26 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 43.31 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 89.74 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 174398.3 | 11KV PVC INSULATED 150SQMM SINGLE CORE X | ISI MARK
7130310042 | 16.0 Sqmm. | km | 58588.78 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 85098.78 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310005 | 25 Sq.mm. | km | 135241.73 | 11KV PVC INSULATED 25SQMM 4 CORE ARMOURE
7130310049 | 120 Sq.mm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310050 | 400 Sqmm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310051 | 3x95 Sq.mm. | km | 1371512.34 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1683609.64
7130310053 | 3x185 Sq.mm. | km | 1924298.52 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 2446944.41 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 23957.22
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 34224.59
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 538738.83 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 763567.97
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 926693.2
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 1082726.04
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 5228.76 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 5502.44 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 80025.06 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 237497.47 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM | ISI MARK
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 237497.47 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310068 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x95+1x16+1x70 | km | 441600.55
7130310092 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x120+1x16+1x95 | km | 551312.67
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 85297.43 | LT AB CABLEB 3X16+1X25 SQMM | ISI MARK
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 86469.51 | LT AB CABLEB 3X25+1X25 SQMM | ISI MARK
7130640032 | 33 kV 3 CORE XLPE UG CABLE 3X 150 SQMM | km | 1943588.25 | 33 kV 3 CORE XLPE UG CABLE 3X 150 SQMM
7130310075 | 33 kV 3 CORE XLPE UG CABLE 3x240 Sq.mm. | km | 2930919.12 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 782172.46 | 11KV 3 CORE XLPE UG CABLE 70 SQMM
7130310077 | 95 Sq.mm | km | 791365.28 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 1180085.11 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 1429802.53 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 2202958.24 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310082 | PVC Insulated 1100 Volts grade Aluminium Twin Core Single Phase 4.0 sq.mm. Unarmoured service cable. | Per Mtr. | 20.16 | PVC Insulated 11kV 2 Core 4.0 sqmm cable
7130310083 | PVC Insulated 1100 Volts grade 70 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 501251.82 | PVC Insul. 70 Sqmm 4C Armour UG AL. Cable
7130310084 | PVC Insulated 1100 Volts grade 95 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 611203.83 | PVC Insul. 95 Sqmm 4C Armour UG AL Cable
7130310085 | PVC Insulated 1100 Volts grade 150 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 922734.53 | PVC Insu. 150 Sqmm 4C Armour UG Al Cable
7130310086 | PVC Insulated 1100 Volts grade 300 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 1762466.07 | PVC Insul. 300 Sqmm. 4C Armour Al. Cable
7130310087 | PVC Insulated 1100 Volts grade 400 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 2240002.75 | PVC Insul. 400 Sqmm. 4C Armour Al. Cable
7130310088 | 33 kV AB Cable Straight thru' joint kit suitable for 185 sqmm | Set | 45506.95 | 33 kV ABC Straight thru jointkit 185 sqmm
7130310089 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 120-240 sq mm XLPE cable | Set | 76738.73 | 33kV UGCable Straight thru jointkit 120-240 sqmm
7130310090 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 300-400 sq mm XLPE cable | No | 85933.91 | 33kV UGCable Straight thru jointkit 300-400 sqmm
7130310652 | 2 Core (UNARMOURED) | Km. | 72362.33 | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310654 | 4 Core (UNARMOURED) | Km. | 132305.02 | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310658 | 8 Core (UNARMOURED) | Km. | 253252.8 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310681 | 10 Core (UNARMOURED) | Km. | 319624.96 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 365803.19 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 329371.81 | CONTROL CABLE COP 12 CORE 2.5 SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 29483.67 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 70493.34 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 95818.1 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 189275.23 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 374426.47 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 469301.42 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC |  | ITEM DELETED: NOT TO BE USED
7130311057 | 150 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV |  | ITEM DELETED: NOT TO BE USED
7130311061 | 300 Sqmm. | km |  | Power Cable ARM ALU 3.5CORE 300/150SQMM |  | ITEM DELETED: NOT TO BE USED
7130311084 | 16.0 Sqmm. | km | 89546.69 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 13689.84
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 17112.3 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 20534.75 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 23957.22 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 25668.45
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 30802.14
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 1077.45 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 1163.86
7130320045 | Cable tie for AB Cable | Each | 34.57
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | No | 5192.06 | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 3311.54 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 3488.72
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 7.24 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 45866.77 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 1110.58 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352031 | 16 Sq.mm, 4 Core | Set | 1110.58 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 1192.67
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1676.66
7130352034 | 150 Sq.mm, 3.5 Core | Set | 2499.15
7130352035 | 300 Sq.mm, 3.5 Core | Set | 4038.97
7130352036 | 400 Sq.mm, 3.5 Core | Set | 5161.06
7130352037 | End terminating jointing kit upto 240 sqmm XLPE cable | Set | 30922.07 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x50 Sq.mm | Set | 18483.6 | 3X50 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352039 | 3x95 Sq.mm | Set | 18483.6 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 24472.89 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 26765.34 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 26765.34 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 9608.12 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 11598.63 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 11932.29 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box (with 10 No. connectors) | No. | 4080.55 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 3.09 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 3.09 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 6.18
7130354277 | 32 Sq mm | Nos. | 7.73
7130354278 | 50 Sq mm | Nos. | 12.39 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 18.57 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 23.21 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 32.51 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 37.14 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 58.81
7130354284 | 225 Sq mm | Nos. | 66.54
7130354285 | 240 Sq mm | Nos. | 95.95
7130354286 | 300 Sq mm | Nos. | 112.98 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 145.48
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 888.45 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 98.54 | INSULATING PIERCING CONNECTOR AB CABLE
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 128.38 | INSULATING PIERCING CONNECTOR FOR AB CABLE
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 178.94 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 161 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 227.52 | STRAIGHT THROUGH JOINT
7130390019 | End cap for 50/70 Sq.mm | Nos. | 38.88 | END CLAMP CAP FOR 50/70 SQMM
7130640040 | M.S. ANGLE 35 x 35 x 5 mm | MT | 38600.4 | M.S. ANGLE 35 x 35 x 5 mm
7130600023 | 50 x 50 x 6 mm | MT | 45520.46 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 45520.46 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 45520.46 | M S ANGLE 75X75X6 MM
7130600166 | 75x40 mm | MT | 45520.46 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 51075.41 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 45520.46 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 51075.41 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT |  | R.S.JOIST 125 x 70 mm |  | ITEM DELETED: NOT TO BE USED
7130600675 | 175 x 85 mm | MT | 56727.95 | R S JOIST 175X85 MM
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 70349.02 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 70349.02 | RAIL 60 KG PER METER
7130601958 | LINE SUPPORTS "H" BEAMS 152x152 mm; 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 53077.58 | H BEAMS 152X152MM; 37.1 KG/MTR.
7130601965 | LINE SUPPORTS "H" BEAMS 152x152 mm; 37.1 Kg/Mtr.; 13 Mtr. Length 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 52664.58 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR
7130600012 | Wide Parallel Flange Beam (WPB) 13 Meter long (160x160 mm) ; 30.44 Kg/Mtr. | MT | 65688.24
7130600011 | Wide Parallel Flange Beam (WPB) 11 Meter long (160x160 mm) ; 30.44 Kg/Mtr. | MT | 65452.24
7130610206 | Barbed wire | MT | 84314.55 | G.I. WIRES: - Barbed wire.
7130810243 | Rack 50x50x6 mm Angle | No | 3872.95
7130620013 | Bolt Big size | No | 155.56 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 86.95
7130620133 | 16x40 mm | Kg | 120.28 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 120.28 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 86.95 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 88.4 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 88.4 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 86.95 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 85.5 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 85.5 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 84.05 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt 25x12 mm | No | 520.75 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 152.82 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | RM | 1106.27 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 958.52 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 4090.22 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work | Cmt | 4090.64
7130300496 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 450 mm | RM | 1769 |  |  | Rate are inclusive of all T&P and labour charges
7130640031 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 600 mm | RM | 2459 |  |  | Rate are inclusive of all T&P and labour charges
7130640036 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 900 mm | RM | 4874 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG) |  | Rate are inclusive of all T&P and labour charges
7130640037 | M.S.Pipe 200 mm dia with collars | RM (medium) | 1504.96
7130640038 | M.S.Pipe 200 mm dia with collars | RM (light) | 1175.3 | M.S. PIPE 200 MM DIA WITH COLLARS
7130640171 | G.I. Bend 40 mm | Each | 106.78
7130641396 | Gl Pipe 40 mm | Per Mtr | 220.62 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | No | 870.41 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4423.96 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. 04-01/ST/62 R2 Date 05.06.2007 | RM | JOB REPLACED |  | Job of Bin code 7130650001 has been raplaced by two types of soil strata as Hard Soil; and Black Cotton Soil | THIS JOB NOT TO BE USED FROM YEAR 2023-24
| Const. of 2.40 M high chain link wire mesh fencing on Hard Soil or Hard Moorum (Non Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete | Mtr. | 2756 |  |  | RATE EXCLUDING G.S.T.
| Const. of 2.40 M high chain link wire mesh fencing on Black Cotton Soil (Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete | Mtr. | 3176 |  |  | RATE EXCLUDING G.S.T.
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 151.17
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 794.21 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 576.46 | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 2371.18 | PCC POLE 140 KG; 8,0 MTR LONG |  | Rate are inclusive of all T&P and labour charges
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 280 Kg; 9.1 Mtr long | Each | 4613.69 | PCC POLE 280 KG; 9.1 MTR LONG |  | Rate are inclusive of all T&P and labour charges
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each |  | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT |  | ITEM DELETED: NOT TO BE USED
7130800672 | 350 Kg; 7.0 Mtr long | Each |  | PCC POLE 350 KG; 7,0 MTR LONG |  | ITEM DELETED: NOT TO BE USED
7130810005 | Through Bolt - 12 mm | No | 109.43 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr Channel 100 x 50 mm. | Set | 7486.37 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810208 | D.C.Cross Arm 4.8 Mtr. Channel 100x50 mm | Set | 9386.55
7130870005 | Stay clamp for 140 kG PCC Pole | Pair | 175.2 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 326.97 | Stay clamp LT/Pair
7130810060 | L.T. "U" Clamp 50x6 mm Flat | No. | 87.6 | LT U CLAMP
7130810213 | Fencing Post 4 Feet Centre 75x75x6 mm | No. | 692.78
7130810214 | Fencing Post 8 Feet Centre 75x75x6 mm | No. | 1386.65
7130810215 | Fencing Post 10 Feet Centre 75x75x6 mm | No. | 1703.35
7130810217 | 33 kV Bird Guard Stool | No. | 252.91
7130810244 | 11 kV Bird Guard Stool | No. | 221.03
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 76.37 | Strain Plate
7130810077 | Pole Clamp | No. | 583.15 | POLE CLAMP
7130810102 | Service Ring | No. | 463.41 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 326.97 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 347.95 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 347.95 | HT STAY CLAMP R S JOIST A TYPE
7130810241 | Stay Clamp for R.S.Joist "B" type | Pair | 347.95
7130810251 | Stay Clamp Rail "B" type | Pair | 347.95 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 347.95 | 33 KV TOP CLAMP SEMIFINISHED
7130810219 | Back Clamp for FRC type Cross Arm | No. | 151.76
7130810220 | Back Clamp for Rail Pole Plate 65x8 mm 1 No. | No. | 347.95
7130810212 | 33 kV Bridling Top Clamps 75x75x6 mm | No. | 421.16
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 679.57 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 809.34 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 939.1 | LT FIVE PIN CROSS ARM
7130810196 | L.T. 2 Pin Cross Arm 50x50x5 mm | No. | 466.25
7130810197 | L.T. 3 Pin Cross Arm 50x50x5 mm | No. | 569.62
7130810198 | L.T. 4 Pin Cross Arm 50x50x5 mm | No. | 674.09
7130810199 | L.T. 5 Pin Cross Arm 50x50x5 mm | No. | 777.44
7130810200 | L.T. 3 Pin Cross Arm 65x65x6 mm | No. | 712.57
7130810202 | L.T. 5 Pin Cross Arm 65x65x6 mm | No. | 997.38
7130810203 | L.T. 5 Pin Cross Arm for tangent location | No. | 1120.54
7130810239 | L.T. Side Bracket 4 Pin 50x50x6 mm | No. | 803.84
7130810240 | L.T. Side Bracket 5 Pin 50x50x6 mm | No. | 3367.11
7130810495 | 11 kV Cross Arm Cleat type | No. | 1152.42 | 11 KV V CROSS ARM
7130810209 | 11 kV Bridling Cross Arm 65x65x6 mm | No. | 1709.94
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 1826.51 | D.O. / LA Mounting channel 75x40 mm.
7130810218 | D.O.Mounting Angle 75x75x6 mm | No. | 1739.08
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2732.61 | 1.1 MTR DPDC CROSS ARM
7130810231 | 11 kV Guarding Angle 100x100x6 mm | Set | 2570.96
7130810232 | Upper & Lower Cross Arm for special structures | Set | 11676
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 4332.59 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810513 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 3147.18 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810234 | D.C.Cross arm 4' Centre for special structures | Set | 4390.87
7130810514 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4422.77 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 5000.08 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810222 | D.C.Cross arm 8' Centre 75x40 mm Channel | Set | 3645.31
7130810223 | D.C.Cross arm 8' Centre Angle type 100x100x6 mm | Set | 5064.95
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2564.36 | 33 KV V CROSS ARM
7130810211 | 33 kV Bridling Cross Arm 75x75x6 mm | No. | 2001.35
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5912.78 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810221 | D.C.Cross arm 5' Centre Angle type 100x100x8 mm | Set | 8489.24
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 101.05 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 426.66 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 323.29 | 11 kV top clamp
7130810210 | 11 kV Bridling Top Clamps 65x65x6 mm | No. | 609.21
7130810204 | 11 kV Cross Arm angle type 65x65x6 mm | No. | 1146.93
7130810205 | 11 kV "V" Cross Arm Channel type 75x40 mm | No. | 1411.94
7130810206 | 11 kV Top Clamp Channel type 75x40 mm | No. | 388.17
7130810207 | 11 kV Top Clamp Cleat type | No. | 285.9
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3548.55 | 11 kV Cut point channel paint
7130810236 | Single Pole Cut Point Fitting 75x40 mm | Set | 1818.8
7130810237 | Side Cross Arm for 11 kV 50x50x6 mm | No. | 2149.8
7130810238 | Side Cross Arm for 11 kV 75x40 mm channel | No. | 2552.26
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 9299.67 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 362.75 | Stay clamp for 'H' Beam
7130810242 | Stay Clamp L.T. Rail for H-Beam | Pair | 347.95
7130820008 | 11 kV Pin insulator with Pin | Each | 139.71 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 378.54 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 111.39 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 187.29 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 5.13 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 599.74 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 2452.66 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 43.21
7130820030 | Disc insulator | Each | 314.39 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 60.51 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 310.47 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 14.36 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 16.99 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 13.68 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 95.84 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 318.93 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 50.75 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 47.98 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 54.62 | HARDWARE FOR 75X90 MM LT SHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 160.75 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 333.97 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2861.66 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 221.56 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km |  | CONDUCTOR AAA SQURREL |  | ITEM DELETED: NOT TO BE USED
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km |  | CONDUCTOR AAA WEASEL |  | ITEM DELETED: NOT TO BE USED
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km |  | CONDUCTOR AAA RABBIT |  | ITEM DELETED: NOT TO BE USED
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km |  | CONDUCTOR AAA RACOON |  | ITEM DELETED: NOT TO BE USED
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 51.51 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 201.06 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 1055.83
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 23770.24 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq) | ISI MARK
7130830054 | Bimetallic clamp for VCB | Each | 616.6
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 36110.28 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq) | ISI MARK
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 616.6
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 60086.82 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q) | ISI MARK
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 313.46
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 89510.94 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E | ISI MARK
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 120401.41 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq) | ISI MARK
7130830070 | 0.2 Sq inch ( 200 Sqmm Al.Eq.)(Panther) | Km | 266865.51 | CONDUCTOR ACSR PANTHER 200 sq mm | ISI MARK
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km |  | CONDUCTOR AAA DOG |  | ITEM DELETED: NOT TO BE USED
7130830585 | T-Clamp for Dog Conductor. | Each | 380.53 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 304.09 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830002 | T-Clamp for Panther Conductor. | Each | 445.33 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 459.86 | Bimetallic clamps for transformer & kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 41.54 | SLEEVE JOINTING ALUMINIUM FOR 0.03 SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 310.74 | SLEEVE REPAIR ALUMINIUM FOR .2 SQ INCH AC
7130840021 | 33 kV Porcelain Lightning Arrestor | Each | 4289.09 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 327.8 | LIGHTNING ARRESTORS 11 KV gapless type.
7130850198 | GI Structure for complete Equipment | Kg | 84.31
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 5000.08 | Transformer mounting 100 x 50 mm channel
7130810224 | Transformer Mounting 75x40 mm Channel | Set | 3645.31
7130850203 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4830.74 | Transformer mounting 100 x 50 mm channel
7130810227 | Bracing Set 4' Centre D.P. | Set | 4047.79
7130810228 | Bracing Set 5' Centre D.P. | Set | 5401.45
7130810229 | Bracing Set 8' Centre D.P. | Set | 4973.68
7130810230 | Bracing Cross Arm for 4 Pole Structures | Set | 10776.49
7130860017 | I-Bolt - 16 mm | No. | 131.84 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 592.97 | STAY SET WITHOUT STAY WIRE 16 mm Paint 11 KV
7130860033 | Stay Set 20 mm (Painted) | Each | 1080.47 | STAY SET WITHOUT STAY WIRE 20 mm (Painted)
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 87273.82 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 88128.62 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 997.81
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 143.69 | EARTHING COIL 8SWG GI WIRE 50 MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 448.38 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 69873.22 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 69823.35 | G.I. WIRES: - 4.0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 69823.35 | G.I. WIRES: - 5.0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 2238.1
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 1315.11 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 3137.26 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2788.67 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 143.01 | CABLE MARKER FOR U/G CABLE
7130880007 | Pad Connector (for Panther conductor) | No. | 181.84 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 101.61 | Danger boards 33 KV & 11 KV.
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 5709.28 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 7203.73
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 16338.04 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 17116.04 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 60.21 | LT LINE SPACERS
7130890973 | Stainless steel strap with buckle (for installation of Service Distribution Box) | Set | 63.44
7131961526 | Modem (4G) | Nos. | 4665.77 | MODEM
7130893004 | Eye Hook | No. | 237.57 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3645.31 | 33 KV guarding channel 100x50 mm.
7130810233 | Railway Cross Structures | Set | 19357
7130810235 | Railway Pole Jointing Channel | Set | 1851.8
7131210001 | Panel lndication lamps | Nos. | 135.12
7131210010 | LED 7 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210018 | LED 12 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210019 | LED 14 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210020 | LED 15 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210021 | LED Lamps with COMPLETE FITTING - 15 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210022 | LED LAMPS WITH COMPLETE FITTING - 20 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210852 | CFL 7 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210881 | 250 Watt Metal Halide | Each |  | METAL HALIDE LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131220182 | Tube Light Rod (T5 type) | Each |  | LAMPS: -Tube Light (40 Watts.) |  | ITEM DELETED: NOT TO BE USED
7131230003 | 250 Watt Sodium Vapour | Each |  | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER |  | ITEM DELETED: NOT TO BE USED
7131230116 | 250 Watt Mercury Vapour | Each |  | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO |  | ITEM DELETED: NOT TO BE USED
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each |  | S/ V HIGH PRESSURE LAMP 400W 230/250V |  | ITEM DELETED: NOT TO BE USED
7131280006 | CFL 15 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280007 | CFL 20 Watts | Each |  | CFL 20 WATTS LAMP |  | ITEM DELETED: NOT TO BE USED
7131280008 | CFL 23 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280009 | 125 Watt Mercury Vapour | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280010 | Halogen Filament (1000 Watts) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280012 | Street Light fitting with tube light | Each |  | STREET LIGHT FITTING WITH TUBE LIGHT |  | ITEM DELETED: NOT TO BE USED
7131280013 | Street Light fitting with CFL | Each |  | STREET LIGHT FITTING WITH CFL |  | ITEM DELETED: NOT TO BE USED
7131280014 | HPSV lamp 150 watt | Each |  | HPSV LAMP 150 WATT |  | ITEM DELETED: NOT TO BE USED
7131280015 | HPSV Choke 250 watt | Each |  | HPSV LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each |  | 150 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each |  | 250 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280882 | CFL 11 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 1975.28 | ENERGY METER ENECTRONIC 10-60 AMPS | ISI MARK
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for __/110 Volts; __/1 Amps; or __/5 Amps) | Each | 1575300 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 191.63 |  |  | RATE EXCLUDING G.S.T.
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 917.98 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 858.9 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A | ISI MARK
7131300881 | CMRI (Common Meter Reading Instrument) | Each | 28091.6 | Common Meter Reading Instrument CMRI
7131310002 | CT operated electronic static bidirectional meter with DLMS for net metering | Each | 3537.38
7131310005 | CT operated electronic static bidirectional meters with DLMS protocol for net metering | Each | 3433.69
7131310045 | Bidirectional Meter 1 phase for Solar Roof Top | Each | 1216.2
7131310040 | Bidirectional Meter 3 phase for Solar Roof Top | Each | 2533.76
7131310013 | 3 Ø 4 Wire 0.5S, 5 Amp. Bulk consumer meter | Each | 5411.58 | HT TRIVECTOR METER 5 AMPS | ISI MARK
7131310015 | CT operated electronic static meters with AMR (Composite Unit) with LTCTs / Modem / Meter / Meter Box. | Each | 15351.14 | ELECTORNIC LTCT METER 3X4 100/5 A | ISI MARK
7131310033 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | Each | 4787.15 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310034 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category B | Each | 4787.15 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310035 | 3 Ø 4 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 27140 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310036 | 3 Ø 3 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 22450.99 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310042 | 3 Ø 4 Wire 0.2S 5A bulk consumer meter | Each | 29182.22 |  | ISI MARK
7131397678 | Test terminal Box (TTB) | Each | 2223.5 | TTB
7131310997 | CT operated electronic static bidirectional meters with DLMS Protocol. | Each | 2075.36 | 3 PHASE 4 WIRE LTCT OPERATED METER | ISI MARK
7131320009 | Digital Multimeter Electronic Type | Nos. | 3748.4 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) Digital | Nos. | 4730.03 |  |  | RATE EXCLUDING G.S.T.
7131324780 | Megger 500 V | Nos. | 4498.07
7131324806 | Megger up to 2.5 kV | Nos. | 6779.28 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 9186.23
7131334001 | Set of 3 O.C. relays + 1 E/F instantaneous high set feature numerical type | Nos. | 8466.5 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C. + 1 earth fault relay without numerical instantaneous high set feature | Nos. | 8608.43 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1339.85
7131300008 | Auxiliary Relay | Nos. | 3486.52
7131300009 | Electrically Reset type Master Trip relay | Nos. | 3891.96
7131300010 | SCADA Compatible Relay (As per IEC 107/IEC61850 protocol) | Nos. | 40195.64
7131338004 | Transformer Oil Dielectric Breakdown testkit | Nos. | 76047.97 |  |  | RATE EXCLUDING G.S.T.
7131338025 | Neon tester | Nos. | 72.35 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 310.89
7131387502 | Thermometer (Wall Mounted) | Nos. | 615.08 | THERMOMETER (WALL MOUNTED)
7131390014 | Earthing Coil for messenger wire | Nos. | 249.92
7131390015 | Anchor sleeve for messenger wire | Nos. | 43.21
7131390016 | Universal hook & Bolts & nuts | Nos. | 605.45
7131820031 | LT Single Phase MCB 5 Amps. | Each | 131.01
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 131.01 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 555.21
7131820034 | LT Three Phase MCB 32 Amps. | Each | 555.21
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 3698.38
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 4007.12
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 4007.12
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2927.84
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 6704.05 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900005 | Locally fabricated - 3 Phase fuse units 150 Amps. (Robust fuse for circuit base). | Each | 988.84 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 9.12 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 366.33 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 563.19 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 15.63 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 16.94 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 361.12 | H.R.C. FUSE UNITS: -100 Amps.
7131900807 | H.R.C. Fuse 100 Amps. | Each | 140.8 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 907.36 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 1003.84 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 1248.1 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 1248.1 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 10 SWG
7131900974 | T.C. Fuse Wire 8 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 8 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 57.94 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 114.49 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 33.11 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 306.25 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 673.19 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 1235.82 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920001 | Load break switches only without panel | Unit | 53857.26 | LOAD BREAK SWITCH WITHOUT PANEL
7131920002 | Load break switches with panel | Unit | 117398.63 | LOAD BREAK SWITCH WITH PANEL
7131920003 | 3 Way Load break switch | Unit | 379797.6 | 3 WAY LOAD BREAK SWITCH
7131920112 | 11 kV Kiosk VCB | Each | 420462.61 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 960.3 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 2305.88 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 4460.3 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 6261.77 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 8495.6 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 12832.35 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  |  | 51.2435
7131930109 | 33 kV ; 600 Amps with earth switch. | Each |  | 33 KV 600 AMPS WITH EARTH SWITCH ISOLATO |  | ITEM DELETED: NOT TO BE USED
7131930221 | 11 kV Porcelain A.B. Switch | Each | 10471.34 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 23249.28 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1237.27 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 3310.46 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 26094.57 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 45159.49 | 33 KV Isolator 800A without earth switch
7131931091 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | Set | 34350.79
7131931095 | Mounting GI structure for above isolator | Set | 14583.18
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 3082.2 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 29280.91 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 29280.91
7131940871 | Indoor Type Automatic Control Unit along with APFC Relay | No. | 57681.32
7131941762 | 11 kV VCB without control panel & CT's. | Each | 154192.41 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 280899.21 | 33KV VCB FOR 30 VOLT DC
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1331.11 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1603.46 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 50551.61
7131950016 | 11 kV Sectionalizer. | Each | 446178.57
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 18891.13 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 23614.9 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 47227.82 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 40524.33 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131950208 | SMC LT Distribution Box for 100 kVA Distribution Transformer | Each | 15533.64
7131950209 | SMC LT Distribution Box for 315 kVA Distribution Transformer | Each | 22892.01
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 28893.09 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 31900.75 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 28124.69 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 29632.55 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960010 | 11 kV Control & Relay Panel for Capacitor Bank | Each | 91055.26
7131960520 | 2 Feeder Control (Static Relays) | Each | 42122.51 | 11KV MULTICIRCUIT (2F) CONTROL PANELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 42392.8 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 43018.74 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm; 3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 224.48
7132004003 | Hack saw frames + B185 | Nos. | 143.91
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 15.1
7132011171 | Cable Cutter | Nos. | 530.56
7132013331 | Discharge Rod | Nos. | 539.91 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 3698.44
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 1436.34
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 444.41
7132061858 | Combination Plier / Cutting Plier | Nos. | 247.05 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 79.9 | SCREW DRIVER 250MM
7132072004 | Screw driver 200 mm | Nos. | 74.83 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 69.76 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. |  | SCREW DRIVER INSULATED 255 MM |  | ITEM DELETED: NOT TO BE USED
7132074032 | Ring Spanners (6x7,8x9,10x11,12x13, 14x15,16x17,18x19,20x22x,21x23, 24x27,25x28,30x32) | Set. | 1740.05 | RING SPANNER
7132074033 | Tube Spanners | Set. | 719.1
7132074034 | Double end spanner (6x7,8x9,10x11, 12x13,14x15,16x17,18x19,20x22x, 21x23,24x27,25x28,30x32) | Set. | 823.1 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 533.93
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F & tommy Bar) | Set. | 1585.32 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1321.44
7132088615 | Pipe Wrench 18 inches size | Nos. | 725.21
7132200014 | 1089 kVAR, 12.1 kV, 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kVAR + 726 kVAR 12.1 KV. Bank shall be complete with Capacitor units of 121 kVAR at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin / Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | Each | 174623.28 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 2117.99 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 4234.66 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 5088.22 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 8444.12 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 230907.67 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each |  | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 25KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 63KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 100KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 200KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210012 | 315 kVA (CEA Design) Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | XMER 315KVA 11/0.43KV CEA REG. CU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210015 | 500 kVA [CEA Design] Copper Wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer |  | ITEM DELETED: NOT TO BE USED
7132210106 | 0.2% Reactor suitable for 363 kVAR step | Set | 8479.9
7132210108 | 0.2% Reactor suitable for 726 kVAR step | Set | 10352.43
7132210215 | 50 kVA (Copper winding) 33/0.4 kV | Each | 251830.58 | TRANSFORMER 33/.4KV 50KVA
7132220091 | Power Transformer 1600 kVA | Each | 1500128.26 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 33/11 KV 3150 kVA | Each | 4456033.02 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 33/11 KV 5000 kVA | Each | 6078909.05 | TRANSFORMER 33/11KV 5 MVA POWER
7132220092 | Power Transformer 33/11 KV 8000 kVA | Each | 8585074.33 | TRANSFORMER 33/11KV 8 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 267615.99 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 527.46 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 247011.43 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 313.29 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 306.8 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 306.8 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1-1A | No. | 765668.4 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 20221.34 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1-1A | No. | 379690.42 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1-1A | No. | 578052.83 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1-1A | No. | 966723.73 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1-1A | No. | 695772.88 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1-1A | No. | 779566.92 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 47130.87
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 107545.2 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 18154.3 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 15178.97 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132200005 | 11 kV C.T. 500-250/5-5 Amps. | Each | 20686.37
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 24806.55 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5-5) Amps oil filled | Each | 25114.47 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each |  | 33KV CT's (100-50/5)A oil filled OD Type |  | ITEM DELETED: NOT TO BE USED
7132230330 | 132 kV C.T. 100-50/1-1A | No. | 730790.17 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1-1A | No. | 541345.24 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1-1A | No. | 347506.34 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A |  | ITEM DELETED: NOT TO BE USED
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 46126.52 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A |  | ITEM DELETED: NOT TO BE USED
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 47126.62 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 42464.01 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A |  | ITEM DELETED: NOT TO BE USED
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 46601.35 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230538 | 11 kV CTPT Unit 50/5 A | Each | 42223.13 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230543 | 132 kV C.T. 100/1 A | No. | 612282.8
7132230544 | 132 kV C.T. 200/1 A | No. | 531661.4
7132230545 | 220 kV C.T. 800/1 A | No. | 641365.19
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 79231.77 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 103432.83 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A |  | ITEM DELETED: NOT TO BE USED
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 86517.16 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A |  | ITEM DELETED: NOT TO BE USED
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 78269.35 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 79399.73 | OIL IMM 3 PH CTPT UNITS 33 KV-100 & 200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 79399.73 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230458 | 33 kV CTPT Unit 400/5A | Each | 75595.51 | OIL IMMERSED 3 PHASE CTPT UNITS 400/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 105928 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230411 | 33 kV CTPT Unit 300/5A | Each | 79399.73
7132230471 | 11 kV 3 PH Residual Voltage Transformer | Each | 41166.48
7132230473 | 11 kV PT Station Type | No. |  |  |  | ITEM DELETED: NOT TO BE USED
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 14164.44 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 22774.85 | VOLTAGE TRANSFORMER 33 KV / 110 VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 466237.64 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 843207.67 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132404015 | Safety belts | Nos. | 697.82 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 162.57 | SAFETY HELMETS
7132404366 | Battery | No. | 67787.02 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 197.85 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 3297.37 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406793 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 4124.76
7132406795 | Pilfer proof Single Compartment SMC meter box for LTCT meters 150/5A with CT | Each | 4896.43
7132406794 | Pilfer proof Single Compartment SMC meter box for LTCT meters 300/5A with CT | Each | 4470.9
7132406425 | Universal Meter Box for HT meters. | Each | ITEM DELETED | Universal Meter Box for HT meters. |  | ITEM DELETED: NOT TO BE USED
7132404529 | Sheet Metal deep drawn HT Meter Box | Each | 4765.89
7132406791 | Sheet Metal deep Drawn Meter Box for LTCT operated meter | Each | 6875.8
7132406721 | CT operated electronic static meters with DLMS. | Each | 3089.55 | LTCT METER WITH DLMS | ISI MARK
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 1675.6 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 6562.35 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 892.42 | RAIN COATS WITH HOODS |  | RATE EXCLUDING G.S.T.
7132427635 | Gum Boots | Nos. | 594.9 | GUM BOOTS |  | RATE EXCLUDING G.S.T.
7132438002 | Silica gel | Kg | 206.57 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 5.84 | POLYCARBONATE SEAL
7132444006 | Holographic Sticker Seal | Each | 2.78
7132444007 | Grounding Sticks (Galvanised Earthing Rods 25 mm, 3 Mtr. long) | Set. | 1028.41
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 6133.6 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 413.82
7132457795 | EHV Gr-I TRANSFORMER OI In Barrel | KL | 89113.6 | TRANSFORMER OIL In Tanker/barrel
7132457800 | EHV Gr-I TRANSFORMER OIL In Tanker | KL | 83343.4 | TRANSFORMER OIL In Tanker/barrel
7132494004 | Fabricated Transformer Oil Storage Tank (10 Kl Capacity) | No. | 438497.86 | Fabricated Transformer Oil Storage Tank
7132459005 | Poly Carbonate seal double anker type | Each | 7 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | ITEM DELETED | HDPE PIPE 200MM ID; 240MM OD |  | ITEM DELETED NOT TO BE USED
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 560.41 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 17700 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 393.26
7132479016 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 153.92 |  |  | RATE EXCLUDING G.S.T.
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 17.63 | PVC INSULATION TAPES 19 MM WIDE AND IN R |  | RATE EXCLUDING G.S.T.
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 83.43 |  |  | RATE EXCLUDING G.S.T.
7132478004 | Tong tester Digital (1000 A, 500 V) with associated accessories | Nos. | 1913.64 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 786.36 | HAND TORCH 5 CELLED
7132478012 | Hand Torch 3 cell | Nos. | 515.55 | HAND TORCH 3 CELLED
7132470004 | Cotton Waste | Kg | 84.11 |  |  | RATE EXCLUDING G.S.T.
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 5868.51 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 75.51 |  |  | RATE EXCLUDING G.S.T.
7132490053 | Bitumen compound | Kg | 135.92
7132498006 | River sand | Cmt | 737.1 | RIVER SAND
7130310027 | 11 kV Covered Conductor 50 Sqmm XLPE insulation | Mtr. | 354.22 | 11KV COVERED CONDUCTOR XLPE 50SQMM
7130310029 | 11 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 394.13 | 11KV COVERED CONDUCTOR XLPE 70SQMM
7130310002 | 11 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 437.83 | 11KV COVERED CONDUCTOR XLPE 99SQMM
7130310047 | 33 kV Covered Conductor 157 Sqmm XLPE insulation | Mtr. | 719.53 | 33KV COVERED CONDUCTOR XLPE 157SQMM
7130310048 | 33 kV Covered Conductor 241 Sqmm XLPE insulation | Mtr. | 856.83 | 33KV COVERED CONDUCTOR XLPE 241SQMM
7130310045 | 33 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 532.63 | 33KV COVERED CONDUCTOR XLPE 70SQMM
7130310046 | 33 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 582.21 | 33KV COVERED CONDUCTOR XLPE 99SQMM
ACCESSORIES FOR COVERED CONDUCTOR :-
7130320050 | (i) Tension / anchoring Clamp with tracking protection IPC | No | 1218.98 | Tension/anchoring Clamp with tracking protection
7130320051 | (ii) Alignment tie (non-metallic) | No | 488.82 | Alignment tie (non-metallic)
7130320052 | (iii) Mechanical conductor with heat shrunk sleeve for bare to covered | No | 1194.48 | Mechanical conductor with heat shrunk sleeve for bare to covered
7130320054 | (iv) IPC for Networking / Branching / Looping CC to CC | No | 1071.97 | IPC for Networking / Branching / Looping CC to CC
7130320055 | (v) IPC with Aluminium Bail for earthing | No | 1255.74 | IPC with Aluminium Bail for earthing
7130320056 | (vi) Mid span joint | No | 673.81 | Mid span joint
7130320057 | (vii) IPC with Aluminium Bail & Transformer Tap (Line this) | No | 1255.74 | IPC with Aluminium Bail & Transformer Tap (Line this)
7130320058 | (viii) Heat Shrinkable End Cap | No | 24.5 | Heat Shrinkable End Cap
7130320059 | (ix) Termination kit / Lug for Transformer Connection | No | 673.81 | Termination kit/Lug for Transformer Connection
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 24159.44 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 37310.86 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 233847.1 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 336819.47 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7131310168 | Spot Billing Machine | Each | 13938.4
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 11 kV CTPT Unit 200/5 Amp | Each | 44511.97 |  |  | ITEM DELETED EARLIER, RE-ADDED
7132230403 | 11 kV CTPT Unit 100/5 Amp | Each | 40501.33
7131900012 | C&R Panel with 3 O/C + 1 E/F relay and Master Trip | Each | 50976
7131900014 | Transformer Auxiliary panel with auxiliary protection relay | Each | 12797.78
7131900015 | 33 kV + 11 kV Transformer Protection Panel (including Transformer auxiliary panel) | Each | 55814
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 42819.58
7130870040 | G.I.Strip 25x3 mm | Kg | 88.08
7130640039 | M.S.Strip 25x3 mm. (0.6 kg/Mtr.) | Kg | 42.63 | M.S.Strip 25x3 mm.
7132444008 | Numerical Poly Carbonate seals | No | 10.76
7130820013 | 33 kV Polymer Disc Insulator (45 kN) | No | 187.29
7131930110 | D.O.Fuse Polymer unit 11 kV | Each | 1506.92
7131930111 | D.O.Fuse Polymer unit 33 kV | Each | 2156.64
7130800001 | PCC Pole 200 kG; 9.0 Mtr. Long | Each | 3195.95 |  |  | Rate are inclusive of all T&P and labour charges
7130800002 | PCC Pole 365 kG; 11 Mtr. Long | Each | 7887.84 |  |  | Rate are inclusive of all T&P and labour charges
7130820001 | 11 kV Polymer Post Insulator | Nos. | 252.87
7130820002 | 33 kV Polymer Post Insulator | Nos. | 963.99
7130820020 | Silicon rubber composite insulator / 11 kV 45 kN Polymeric Insulator | Nos. | 111.39
7131930220 | Polymer A.B.Switch with complete fitting 11 kV | Each | 7998.21
7131930320 | Polymer A.B.Switch with complete fitting 33 kV | Each | 18927.97
7130800032 | 200 Kg 8.0 Meter long PCC Pole | No | 2673.36 |  |  | Rate are inclusive of all T&P and labour charges
7130311023 | 2.5 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 33.24 | 2.5 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311024 | 4.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 39.88 | 4.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311025 | 6.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 58.16 | 6.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311026 | 6.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 69.79 | 6.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311027 | 8.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 84.75 | 8.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311028 | 10 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 101.37 | 10 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311029 | 16 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 132.96 | 16 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311030 | 25 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 169.51 | 25 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311085 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 258498.93 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables
7132210017 | 16 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 77310.58 | XMER 16KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210018 | 25 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 65016.7 | XMER 25KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210019 | 63 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 125345.25 | XMER 63KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210020 | 100 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 164821.1 | XMER 100KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210021 | 200 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 352684.76 | XMER 200KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132220081 | 315 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 1071277.58 |  | ISI MARK
7132220082 | 500 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 1521670.31 |  | ISI MARK
7132210022 | 25 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 78621.18
7132210023 | 63 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 135219.73
7132210024 | 100 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 165773.86
7132210025 | 200 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 354119.68
7132210027 | 315 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 965414.75
7132210028 | 25 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 82528.82
7132210029 | 63 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 148218.56
7132210030 | 100 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 192133.46
7132220085 | 315 kVA Copper Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With HV & LV side Box) | Each | 1087040.36
7132220086 | 500 kVA Copper Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With HV & LV side Box) | Each | 1547700.56
7130640008 | RCC Block (with 6 mm MS Bar) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130300055 | Round Shape RCC Base Plate(with 6mm MS Bar) | Each | 173 |  |  | Rate are inclusive of all T&P and labour charges
7130300056 | Square Shape RCC Base Plate(with 6mm MS Bar) | Each | 293 |  |  | Rate are inclusive of all T&P and labour charges
7131210011 | LED 9 Watt Lamp (without holder) | Each | 77 | LED 9 W lamp with holder
7131210009 | LED Tube Light, 20 Watt | Set | 242.01 | LED Tube Light, 20 Watt
7131210030 | 18 W LED Street Light complete set | Set | 2491.08 | 18 W LED Street Light complete set
7131210031 | 35 W LED Street Light complete set | Set | 3217.96 | 35 W LED Street Light complete set
7131210032 | 70 W LED Street Light complete set | Set | 4552.2 | 70 W LED Street Light complete set
7131210033 | 110 W LED Street Light complete set | Set | 6186.43 | 110 W LED Street Light complete set
7131210034 | 190 W LED Street Light complete set | Set | 10910.5 | 190 W LED Street Light complete set
7131210035 | 190 W LED Flood Light complete set | Set | 10585.25 | 190 W LED Flood Light complete set
7131210036 | 110 W LED Flood Light complete set | Set | 7069.16 | 110 W LED Flood Light complete set
7131210023 | LED Lamps with complete fitting-24 W | Nos. |  | 24 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210024 | LED Lamps with complete fitting-48 W | Nos. |  | 48 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210025 | LED Lamps with complete fitting-60 W | Nos. |  | 60 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131941763 | 3 Way RMU, 2OD + 1VL, One Incomer + One Breaker + One Outgoing, 350 MVA, 650 Amps. | Unit | 939353.2 | 11 kV RMU 3 WAY,2 OD+1 VL, 350 MVA, 650 A.
7131941764 | 4 Way RMU, 2OD + 2VL, (One Incomer + Two Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1334322.01 | 11 kV RMU 4 WAY,2 OD+2 VL, 350 MVA, 650 A.
7131941765 | 5 Way RMU, 2OD + 3VL, (One Incomer + Three Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1722255.71 | 11 kV RMU 5 WAY,2 OD+3 VL, 350 MVA, 650 A.
7131941766 | 6 Way RMU, 2OD + 4VL,(One Incomer + Four Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 2110189.41 | 11 kV RMU 6 WAY,2 OD+4 VL, 350 MVA, 650 A.
7131941767 | 1OD for RMU | Unit | 337998.09 | 1OD for RMU
7131941768 | 1VL for 350 MVA, 650 Amps RMU | Unit | 394968.81 | 1VL for 350 MVA, 650 Amps RMU
7132230028 | Indoor Type 33 kV Metering Cubical CTPT Unit 10/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 10/5A CT:PT CUBICAL UNIT
7132230029 | Indoor Type 33 kV Metering Cubical CTPT Unit 25/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 25/5A CT:PT CUBICAL UNIT
7132230030 | Indoor Type 33 kV Metering Cubical CTPT Unit 200/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 200/5A CT:PT CUBICAL UNIT
7132230031 | Indoor Type 11 kV Metering Cubical CTPT Unit 10/5 A | Each | 117805.45 | INDOOR TYPE 11 KV 10/5A CT:PT CUBICAL UNIT
7132230020 | Indoor Type 11 kV Metering Cubical CT-PT Units 15/5 A | Each | 117805.45 | Indoor Type 11kV 15/5A CTPT Cubical Unit
7132230010 | Indoor Type 11 kV Metering Cubical CTPT Unit 25/5 A | Each | 117805.45 | INDOOR TYPE 11 KV 25/5A CT:PT CUBICAL UNIT
7132230027 | Indoor Type 11 kV 50/5 A Metering Cubical CT-PT Units | Each | 117807.48 | Indoor Type 11kV 50/5A CTPT Cubical Unit
7131980004 | (0+1) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH ONE 630 A LOAD BREAK SWITCH. | No. | 285484.83
7131980005 | (0+3) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH THREE 630 A LOAD BREAK SWITCHES. | No. | 527899.18
7131980006 | (0+4) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR 630 A LOAD BREAK SWITCHES. | No. | 640487.09
7131980007 | (0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER IN BETWEEN AFTER ISOLATOR. | No. | 1020610.69
7131980008 | (0+2)+BC+(0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH SIX NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER WITH LBS IN BETWEEN AFTER ISOLATOR. | No. | 1614068.62
7131941001 | Feeder Remote Terminal Unit (FRTU) with accessories Multifunction Transducer (MFT), Contact Multiplication Relay (CMR), Heavy Duty Relay & software. | No. | 105881.18
7131941002 | Compact arrangement of RMU+FRTU+ LT Distribution Box in a closed chamber for 11/0.433 kV Distribution sub-station (excluding Distribution Transformer) with Transformer in top & RMU+FRTU+ LT Distribution Box in bottom, compatible upto 650 kVA. | No. | 1553775.07
7131941003 | Compact arrangement of RMU+FRTU+ LT Distribution Box in a closed chamber for 11/0.433 kV Distribution sub-station (excluding Distribution Transformer) with Transformer in top & RMU+LT Distribution Box in bottom, compatible upto 650 kVA. | No. | 1265446.31
7131980001 | 12 kV, Outdoor type Vacuum Capacitor switches | No. | 83678.8
7131920028 | AC Distribution board for AC/DC Supply | No. | 12330.35
7132486843 | Chem Rod Earthing electrode (Chemical Earthing) [As per specification given in Schedule-C-20] | Job | 9170.44 |  |  | RATE EXCLUDING G.S.T.
7130840003 | Surge Arrestor | No. | 1109.72
7131950396 | Ground connection for Messenger Wire | No. | 168.6
7132406800 | 33/11 kV S/S (Name Plate) Board | Job | 10253.32
7131210840 | 11 kV Fault Passage Indicator for Overhead line | No. | 17780.12 |  |  | RATE EXCLUDING G.S.T.
7132455003 | SMC Meter Board 350x200x40 mm (minimum) thickness 2.5 mm | No. | 162.74 | SMC Meter Board 350x200x40 mm, thickness 2.5 mm
7132455004 | SMC Board 200x150x40 mm (minimum) thickness 2.5 mm | No. | 127.87 | SMC Board 200x150x40 mm thickness 2.5 mm
7131920004 | Piano type ISI mark 250V/5A switch. | No. | 13.82 | Piano type ISI mark 250V/5A switch.
7131920005 | 250V/5A ISI mark 3 pin Socket | No. | 34.55 | 250V/5A ISI mark 3 pin Socket
7131920006 | 250V/5A ISI mark holder. | No. | 20.73 | 250V/5A ISI mark holder.
7131390482 | Earthing terminal (having suitable size of 10 mm Dia GI bolt with 3 nos. nuts & washers) along with Staples/ Nut-Bolts/ Nails | No. | 58.12 | Earth terminal(10mm Dia GI bolt with 3 no) nuts & washers) along with Staples/ Nut-Bolts/ Nails
7130310081 | Internal wiring using 1.5 sqmm copper multistrands PVC insulated ISI marked cable (Average cable length 6 Mtr.) | Mtr | 10.54 | 1.5 sqmm copper multistrand PVC cable
7132461006 | 25 mm Dia PVC pipe or equivalent for internal house wiring (3 Mtr) | Feet | 6.57 | 25 mm Dia PVC pipe or equivalent (3 Mtr)
7132498054 | Bhatta brick | No. | 6.57 | Bhatta brick
7131397216 | Meter Sealing Wire | Kg | 244.83
7132010551 | Hand Operated type 25 sq.mm. to 400 sq.mm Crimping Tool | No. | 9846.82
7132010552 | Hydraulic type Crimping Tool with suitable Dies for crimping Lugs of size up to 400 sq.mm. | Set | 12561.71
7132478005 | RECHARGEABLE L.E.D. HAND TORCH | No. | 865.13 | RECHARGEABLE L.E.D. HAND TORCH
7132089020 | Cable separator in RCC Pipe with Angle Cross of 50x50x6 mm Angle @ 2 No. in one pipe | No. | 735.03 | Cable separator in RCC Pipe with 50x50x6 mm Angle
7132200004 | 11 kV Capacitor Unit with Expulsion Tube | Each | 139.58 |  | (cost per kVAR)
7131310032 | ABT Meter Accuracy class: 0.2s, C.T. Ratio: _/1A, P.T.Ratio: _/110V | No. | 313249.88
7131310048 | 3 Ø 4 Wire ABT meter | No. | 286843.81
7131310049 | 3 Ø 3 Wire ABT meter | No. | 286843.81
| Cost of Galvanization | MT | 26773.02
7132401667 | Office Almirah Storwel plain with 4 shelves 78''x36''x19'' | No. | 15340
7132401205 | Office Almirah Storwel minor plain 50''x30''x17'' | No. | 7552
7132409830 | Office Chair model CH-7 cane seat & back with full arms rest | No. | 4720
Office Table
7132476013 | 5'x3.5'x2.5' | No. | 11918
7132476792 | Model T-8 4'x2' | No. | 16732.4
7132476797 | Model T-9 4.5'x2.25' | No. | 10620
7132476795 | Ex. Table Model T-104 66''x36'' | No. | 25960
7132409025 | Computer Table | No. | 9912
7132409061 | Computer Chair | No. | 5900
7132401672 | Small almirah 50", 20 SWG Sheet | No. | 8024
7132476014 | Office Table 4'x2.5' | No. | 8968
7132409815 | Chair | No. | 2301
7132409819 | Officer Chair | No. | 2832
Steel Rack
7132401669 | 78''x36''x18'' (Heavy) | No. | 7080
7132476016 | 72''x36''x15'' (Heavy) | No. | 4484
7132476799 | 59''x39''x18'' | No. | 5900
7132499008 | PC with Monitor : i3; 4th Gen, 4 GB RAM, 1TB HDD, 18.5” Display (Monitor), Windows 8 | Set | 61950
7132499023 | LAPTOP : i5; 8th Gen, 8 GB RAM, 1TB HDD, Win 10 OS, MS-Office-10 Home Edition, 13.3” Display, | No. | 68440
Laser Printer : B/W
7132499029 | Speed 12 PPM | No. | 17464
7132499044 | Speed 28 PPM (Multi function) | No. | 40120
7132420412 | Fax Machine with print and copy capabilities. | No. | 10620
7132488810 | Photo copier | No. | 48999.5
7132531017 | Scanner : 2400 x 4800 dpi, | No. | 8848.82
7132486006 | Water Purifier | No. | 10785.2
7132486195 | Water Cooler (80 Ltr) | No. | 41300
7132401202 | Air Cooler | No. | 6490
7132420160 | Ceiling Fan (48") [BEE 5 star rating] | No. | 2080.01
7132486151 | Wall Coffer | No. | 11800
7131880133 | Air Conditioner 2 Ton 4 Star (Split) | No. | 48527.5
7131880134 | Air Conditioner 1.5 Ton 4 Star (Split) | No. | 36119.07
7132486004 | UPS 600 VA | No. | 2006
EHV- Gr-1, TRANSFORMER OIL
7130572150 | Contaminated Oil | Ltr | 50.01 |  |  | RATE EXCLUDING G.S.T.
ALUMINIUM ITEMS
7130570050 | Aluminium | Kg | 102 |  |  | RATE EXCLUDING G.S.T.
7130570160 | ACSR Conductor | Kg | 167.7 |  |  | RATE EXCLUDING G.S.T.
7130570925 | Aluminium UG Cable | Kg | 83 |  |  | RATE EXCLUDING G.S.T.
7130570055 | Aluminium Wire in pieces | Kg | 88 |  |  | RATE EXCLUDING G.S.T.
7130570055 | Released Aluminium windings from failed Distribution Transformers | Kg | 94 |  |  | RATE EXCLUDING G.S.T.
7130570185 | Insulated wire / cable aluminium Scrap | Kg | 150 |  |  | RATE EXCLUDING G.S.T.
COPPER ITEMS
7130570167 | Copper Wire | Kg | 794 |  |  | RATE EXCLUDING G.S.T.
7130570167 | Released Copper Windings from failed Distribution Transformers | Kg | 794 |  |  | RATE EXCLUDING G.S.T.
IRON ITEMS
7130570145 | Rail Pole, H-Beam | Kg | 39.11 |  |  | RATE EXCLUDING G.S.T.
7130570200 | Cross Arms, Clamps , MS Scrap etc. | Kg | 42.73 |  |  | RATE EXCLUDING G.S.T.
7130570910 | Barbed Wire / Ground Wire | Kg | 57.51 |  |  | RATE EXCLUDING G.S.T.
7130560870 | TRANSFORMER EMPTY TANKS OF DIFFERENT CAPACITY | Kg | 41 |  |  | RATE EXCLUDING G.S.T.
7130500153 | BROKEN STEEL FURNITURE | Kg | 15 |  |  | RATE EXCLUDING G.S.T.
7130570915 | SCRAP WOODEN FURNITURE | Kg | 6.93 |  |  | RATE EXCLUDING G.S.T.
7130560150 | Empty barrel of 210 litres capacity 200/210 Ltrs. | No. | 287 |  |  | RATE EXCLUDING G.S.T.
7130570205 | Lead | Kg | 121 |  |  | RATE EXCLUDING G.S.T.
7130570125 | Brass | Kg | 443.45 |  |  | RATE EXCLUDING G.S.T.
CTs & PTs
7130530601 | 11 KV CT | No. | 3319.14 |  |  | RATE EXCLUDING G.S.T.
7130530602 | 33 KV CT | No. | 5163.1 |  |  | RATE EXCLUDING G.S.T.
7130530604 | 11 KV PT | No. | 4022.91 |  |  | RATE EXCLUDING G.S.T.
7130530604 | 33 KV PT | No. | 5368 |  |  | RATE EXCLUDING G.S.T.
7130530608 | CT/PT Unit Srap 11 kV | No. | 4425.52 |  |  | RATE EXCLUDING G.S.T.
Energy Meter
7130570230 | Energy Meter (Electro-mech) Single Phase | Kg | 62.9 |  |  | RATE EXCLUDING G.S.T.
7130570230 | Energy Meter (Electro-mech) Three Phase | Kg | 62.9 |  |  | RATE EXCLUDING G.S.T.
7130500152 | Single/Three Phase Electronic Meters | Kg | 99.5 |  |  | RATE EXCLUDING G.S.T.
Scrap Distribution Transformer of Aluminium Winding (without oil)
7130530611 | 16 kVA | Each | 13101 |  |  | RATE EXCLUDING G.S.T.
7130530613 | 25 kVA | Each | 18221 |  |  | RATE EXCLUDING G.S.T.
7130530615 | 63 kVA | Each | 25811 |  |  | RATE EXCLUDING G.S.T.
7130530616 | 100 kVA | Each | 34504 |  |  | RATE EXCLUDING G.S.T.
7130530619 | 200 kVA | Each | 71201 |  |  | RATE EXCLUDING G.S.T.
7130530633 | 315 kVA (Copper Wound) | Each | 225100 |  |  | RATE EXCLUDING G.S.T.
7130530625 | 500 kVA (Copper Wound) | Each | 276315 |  |  | RATE EXCLUDING G.S.T.
7130530611 | Transformer Scrap three Phase 16 kVA Alum. Winding | Each | 14300 |  |  | RATE EXCLUDING G.S.T.
7130530638 | Transformer Scrap Single Phase 16 kVA Copper Winding | No. | 39500 |  |  | RATE EXCLUDING G.S.T.
7130530217 | 33/0.4 KV 63 KVA Transformer Copper Wound | No. | 75506 |  |  | RATE EXCLUDING G.S.T.
7130530223 | 33/0.4 KV 100 KVA Transformer Copper Wound | No. | 659111 |  |  | RATE EXCLUDING G.S.T.
7130500084 | HT Metering Cubicle, Distribution Boxes, feeder piller boxes etc. | Kg | 15 |  |  | RATE EXCLUDING G.S.T.
7130570065 | Automobile parts scrap | Kg | 100 |  |  | RATE EXCLUDING G.S.T.
7130578361 | Pick up Mahindra | No. | 40000 |  |  | RATE EXCLUDING G.S.T.
7132220002 | 3150 kVA, 33/11 kV INDOOR TYPE POWER TRANSFORMER Oil Cooled with Off Circuit Tap Changer with Primary and secondary terminal Box type | Each | 4244979.57 |  |  | RATE EXCLUDING G.S.T.
7132220006 | 5000 kVA, 33/11 kV INDOOR TYPE POWER TRANSFORMER Oil Cooled with Off Circuit Tap Changer with Primary and secondary terminal Box type | Each | 5791627.21 |  |  | RATE EXCLUDING G.S.T.
33 kV Compact Ring Main Unit (RMU) [VCB/SF6 Type] with Aluminium Bus-bar
7131941004 | 3 Way RMU, 2LBS + 1VCB, One Incomer + One Breaker + One Outgoing, SF6 gas, 630 Amps, without FRTU | Unit | 3093346.28 |  |  | RATE EXCLUDING G.S.T.
7131941005 | 4 Way RMU, 2LBS + 2VCB, One Incomer + Two Breakers + One Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 4460868.09 |  |  | RATE EXCLUDING G.S.T.
7131941006 | 3 Way RMU, 3LBS, One Incomer + Two Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 2878364.68 |  |  | RATE EXCLUDING G.S.T.
7131941007 | 4 Way RMU, 4LBS One Incomer + Three Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 3855336.6 |  |  | RATE EXCLUDING G.S.T.
33 kV JOINTING KIT :-
7130352011 | 33 kV End terminating jointing kit TOUCH PROOF upto 240 sqmm XLPE cable | No. | 53784.99 |  |  | RATE EXCLUDING G.S.T.
7130352012 | 33 kV End terminating jointing kit TOUCH PROOF upto 300 sqmm XLPE cable | No. | 57370.66 |  |  | RATE EXCLUDING G.S.T.
7130352013 | 33 kV End terminating jointing kit TOUCH PROOF upto 400 sqmm XLPE cable | No. | 58685.4 |  |  | RATE EXCLUDING G.S.T.
7130352014 | LT End termination jointing kit for 4-core 300 sq.mm. XLPE underground cable | Set | 860.97 |  |  | RATE EXCLUDING G.S.T.
3.5 Core, 1.1 kV LT PVC Armoured Cable :-
7130311015 | 16 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 150 |  |  | RATE EXCLUDING G.S.T.
7130311016 | 25 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 191.86 |  |  | RATE EXCLUDING G.S.T.
7130311017 | 50 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 280.23 |  |  | RATE EXCLUDING G.S.T.
7130311018 | 70 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 367.43 |  |  | RATE EXCLUDING G.S.T.
7130311019 | 95 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 448.83 |  |  | RATE EXCLUDING G.S.T.
7130310093 | 120 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 553.48 |  |  | RATE EXCLUDING G.S.T.
7130311020 | 150 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 656.96 |  |  | RATE EXCLUDING G.S.T.
7130311021 | 185 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 808.12 |  |  | RATE EXCLUDING G.S.T.
7130311031 | 240 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1017.42 |  |  | RATE EXCLUDING G.S.T.
7130311032 | 300 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1236.02 |  |  | RATE EXCLUDING G.S.T.
7130310094 | 400 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1558.11 |  |  | RATE EXCLUDING G.S.T.
7130870011 | Copper Bonded Ground Rod 25 mm, 3 Mtr long (For transformer body and neutral earthing) | No. | 14206.7463 |  |  | RATE EXCLUDING G.S.T.
7130870012 | Copper Bonded Ground Rod 17.2 mm, 3 Mtr long (For earthing of rest of the body) | No. | 11471.81 |  |  | RATE EXCLUDING G.S.T.
7132490002 | Chemical earthing Compound (1 packet of 25 kg) 2 packet per earth pit | Packet | 1353.38 |  |  | RATE EXCLUDING G.S.T.
7130870014 | Copper bonded strip 25x3 mm. (0.65 kg/Mtr) | Mtr. | 333.44 |  |  | RATE EXCLUDING G.S.T.
7132461002 | HDPE Pipe OD 250mm, PN10 PE100, SDR 13.6 made of virgin material | Mtr. | ITEM DELETED |  |  | ITEM DELETED NOT TO BE USED
11/0.4 kV Compact Sub-station
7131941008 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 1600 Amp. +Transformer of 1000 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 6 nos., MCCB rating - 400 Amp. | No. | 4368664.87 |  |  | RATE EXCLUDING G.S.T.
7131941009 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 800 Amp. +Transformer of 500 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 4 nos., MCCB rating - 400 Amp. | No. | 3320749.03 |  |  | RATE EXCLUDING G.S.T.
7131941010 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 630 Amp. +Transformer of 315 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 4 nos., MCCB rating - 200 Amp. | No. | 2701840.91 |  |  | RATE EXCLUDING G.S.T.
7131941011 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 400 Amp. +Transformer of 200 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 2 nos., MCCB rating - 200 Amp. | No. | 2385698.53 |  |  | RATE EXCLUDING G.S.T.
7130310091 | XLPE insulated PVC sheathed 4 core 300 Sq.mm. Armoured LT underground cable | Mtr. | 1239.51 |  |  | RATE EXCLUDING G.S.T.
7131960012 | Indoor, floor mounted 33 KV Transformer control switchboard comprising of 1 vertical panels which horizontal top bus bars of Al, rated for 800 A VCBs , in draw out executions. The VCB shall be rated for 36KV, 1600 A, 26kA. The panels shall be complete with all accessories, hardwares, heater etc. as required for completeness. Panel for controlling 5MVA power transformer with VCB, CTs, PTs,digital meters, Trivector Energy Meters, transformer protection relays, auxiliary relays etc. | Each | 1721033.26 |  |  | RATE EXCLUDING G.S.T.
7131960013 | Indoor, floor mounted 33KV feeder control switchboard comprising of 1 vertical panels which horizontal top bus bars of Al, rated for 800 A VCBs , in draw out executions. The VCB shall be rated for 36KV, 1600 A, 26kA. The panels shall be complete with all accessories, hardwares, heater etc. as required for completeness. Panel for controlling outgoing/ Bus coupler with VCB, CTs, digital Ammeter/voltmeter/ Trivector Energy meter, O/C and E/F relay etc. The cable chamber shall have 3 nos., 20kV, 10 kA distribution class valve type lightning arresters. | Each | 1721033.26 |  |  | RATE EXCLUDING G.S.T.
7131960014 | Indoor, floor mounted 11KV Transformer control switchboard of 01vertical panel with horizontal top bus bars of Al rated for 800 A, VCBs and LBS, in draw out executions. The VCB shall be rated for 12KV, 18.4kA. The panels shall be complete with all accessories, hard wares, heater etc. as required for completeness. Panel for controlling incomer with VCB of 800 A ratings, CTs, PTs, digital Ammeter/ voltmeter/ Trivector Energy meter, O/C and E/F relay etc. | Each | 1182257.4025 |  |  | RATE EXCLUDING G.S.T.
7131960015 | Indoor, floor mounted 11KV feeder control switchboard of 01vertical panel with horizontal top bus bars of Al rated for 800 A, VCBs and LBS, in draw out executions. The VCB shall be rated for 12KV, 18.4kA. The panels shall be complete with all accessories, hard wares, heater etc. as required for completeness. Panel for controlling outgoing feeders with VCB of 400A rating, CTs, digital meter, Trivector Energy Meters, O/C and E/F relay, auxiliary relays etc. | Each | 1182257.4 |  |  | RATE EXCLUDING G.S.T.
7132230001 | 11 kV Current Transformer Resin type, Ratio 200-100/5 Indoor Type | Each | 67006.48 |  |  | RATE EXCLUDING G.S.T.
7132230003 | 11 kV Current Transformer Resin type, Ratio 300-150/5 Indoor Type | Each | 55527.95 |  |  | RATE EXCLUDING G.S.T.
7132230004 | 11KV Potential Transformer Resin type, [Indoor Type] | Each | 125922.46 |  |  | RATE EXCLUDING G.S.T.
7130641035 | G.l. Pipe 150 mm OD (Class B as per railway) | Per Mtr | 1487.06 | G.I. Pipe 150mm
7132461804 | HDPE pipe of size 160 mm OD/140 mm ID PN 10 PE 100 HDR | Per Mtr | 1294.34 | HDPE pipe size 160mm OD/140mm ID PN10
7131950210 | SMC LT Distribution Box for 200 kVA Distribution Transformer | Each | 22892.01 | SMC LT Distribution Box for 200 KVA Xmer
7131382840 | Microprocessor based single phase fully automatic oil BDV Test Kit | No | 250750 | Transformer oil BDV test kit |  | New item introduced
7131300014 | Digital weighing Machine (Range 50 g to 500 kg) | No | 20532 | Digital weighing machine |  | New item introduced
7131300015 | Digital vernier calipers(0-200 mm Range,Accuracy 0.01 mm) | No | 3315.8 | Digital vernier calipers |  | New item introduced
7131300016 | Digital Screw Gauge (0-25 mm Range,Accuracy 0.01 mm) | No | 4576.04 | Digital screw gauge |  | New item introduced
7131300017 | Measuring Tape (30 meter length) | No | 290.28 | Measuring tape |  | New item introduced
7131300018 | Laser Gun( Measure distance upto 125 meter and should be operational during day time also) | No | 20414 | Laser gun |  | New item introduced
7131960101 | MCR panel for 33 KV O/D VCB Feeder protection | EA | 205202 | MCR Panel for 33 KV O/D VCB Feeder Prot. |  | New item introduced
7131960102 | MCR panel for feeder & Capacitor Bank protection 11 KV | EA | 205202 | MCR Panel for Feeder & CapBank Prot 11KV |  | New item introduced
7131960103 | MCR panel for LV | EA | 211574 | MCR Penal for LV |  | New item introduced
7131961532 | RTU base equipment comprising panels,racks, sub-racks, CPU, interfacing equipment, required converters & all other required items/accessories including complete wiring for all modules(with WAN router MPLS connection port & with dual SIM ports and HMI of Min 10 '' Size) | EA | 430700 | Penal Pre wired RTU Integr. with BCPU |  | New item introduced
7130310101 | LAN cable armoured CAT6 (SFTP) | Mtr | 159.3 | LAN Cable Armoured CAT 6 (SFTP) |  | New item introduced
7130640033 | GI Conduit flexible with PVC coating | Mtr | 88.5 | GI Conduit flexible with PVC coating |  | New item introduced
7132468020 | 24 V DCPS with 8 Hrs back up (24 V DCPS to be provided for RTU and MCRP solutions with 3 years battery warranty) | EA | 142190 | 24V DCPS with 8 Hrs Backup |  | New item introduced
7130310105 | Cable 1.1 Kv 4C x 4 Sqmm Cu Unarmoured PVC | Mtr | 312.7 | Cable 1.1KV 4Cx4 Sqmm Cu Unarmoured PVC |  | New item introduced
7130310106 | Control cable 1.1 KV Cu 4C x 2.5 Sqmm Armoured | Mtr | 247.8 | Control Cable 1.1KV Cu 4Cx2.5 Sqmm Armrd |  | New item introduced
7130310109 | Control cable 1.1 KV Cu 10C x 1.5 Sqmm Armoured PVC | Mtr | 348.1 | Control Cable 1.1KV Cu 10Cx1.5 Sqmm Arm. |  | New item introduced
| 11 KV DO Fuse Element:- |  |  |  |  | New item introduced
7131900501 | 1.5 Amp | No | 25.96 | FUSE ELEMENT 1.5 AMPS FOR 11 KV D O |  | New item introduced
7131900504 | 3 Amp | No | 27.14 | FUSE ELEMENT 3 AMPS FOR 11 KV D O |  | New item introduced
7131900505 | 5 Amp | No | 28.32 | FUSE ELEMENT 5 AMPS FOR 11 KV D O |  | New item introduced
7131900525 | 25 Amp | No | 25.96 | FUSE ELEMENT 25 AMPS FOR 11 KV D O |  | New item introduced
7130310108 | Single core XLPE insulated, PVC sheathed unarmoured cable : - 400 Sqmm | Km. | 431043.65 | 1CX 400 SQMM(AL) XLPE, PVC SHEATED UNARM |  | New item introduced
7132504016 | 32 Volts 100 AH Lithium Ferro Battery | No. | 96760 | 32V 100AH Lithium ferro phosphate battry |  | New item introduced
7131961530 | Modem(NBIoT) | Nos. | 5780.82 | NBIoT Modems |  | New item introduced
7130530610 | CT/PT Unit Scrap 33 KV | No. | 17702.09 | PT SCRAP 33 KV |  | New item introduced
Note on B154: Author: old name I-Bolt (big size)
Note on D190: Author: GST applicable separately.
Note on D191: Author: GST applicable separately.
Note on D381: Author: GST applicable separately.
Note on D399: Author: GST applicable separately.
Note on D409: Author: GST applicable separately.
Note on A432: Author: bin code changed old bin no was 7131900875
Note on D598: Author: GST applicable separately.
Note on D599: Author: GST applicable separately.
Note on D614: Author: GST applicable separately.
Note on D615: Author: GST applicable separately.
Note on D616: Author: GST applicable separately.
Note on D620: Author: GST applicable separately.
Note on D622: Author: GST applicable separately.
Note on D732: Author: GST applicable separately.
Note on D736: Author: GST applicable separately.
Note on D791: Author: GST applicable separately.
Note on D793: Author: GST applicable separately.
Note on D794: Author: GST applicable separately.
Note on D795: Author: GST applicable separately.
Note on D796: Author: GST applicable separately.
Note on D797: Author: GST applicable separately.
Note on D798: Author: GST applicable separately.
Note on D800: Author: GST applicable separately.
Note on D801: Author: GST applicable separately.
Note on D803: Author: GST applicable separately.
Note on D804: Author: GST applicable separately.
Note on D805: Author: GST applicable separately.
Note on D806: Author: GST applicable separately.
Note on D807: Author: GST applicable separately.
Note on D808: Author: GST applicable separately.
Note on D809: Author: GST applicable separately.
Note on D810: Author: GST applicable separately.
Note on D811: Author: GST applicable separately.
Note on D813: Author: GST applicable separately.
Note on D814: Author: GST applicable separately.
Note on D815: Author: GST applicable separately.
Note on D816: Author: GST applicable separately.
Note on D817: Author: GST applicable separately.
Note on D819: Author: GST applicable separately.
Note on D820: Author: GST applicable separately.
Note on D821: Author: GST applicable separately.
Note on D823: Author: GST applicable separately.
Note on D824: Author: GST applicable separately.
Note on D825: Author: GST applicable separately.
Note on D826: Author: GST applicable separately.
Note on D827: Author: GST applicable separately.
Note on D828: Author: GST applicable separately.
Note on D829: Author: GST applicable separately.
Note on D830: Author: GST applicable separately.
Note on D831: Author: GST applicable separately.
Note on D832: Author: GST applicable separately.
Note on D833: Author: GST applicable separately.
Note on D834: Author: GST applicable separately.
Note on D835: Author: GST applicable separately.
Note on D836: Author: GST applicable separately.
Note on D837: Author: GST applicable separately.
Note on D838: Author: GST applicable separately.
Note on D840: Author: GST applicable separately.
Note on D841: Author: GST applicable separately.
Note on D842: Author: GST applicable separately.
Note on D843: Author: GST applicable separately.
Note on D845: Author: GST applicable separately.
Note on D846: Author: GST applicable separately.
Note on D847: Author: GST applicable separately.
Note on D848: Author: GST applicable separately.
Note on D850: Author: GST applicable separately.
Note on D851: Author: GST applicable separately.
Note on D852: Author: GST applicable separately.
Note on D853: Author: GST applicable separately.
Note on D854: Author: GST applicable separately.
Note on D855: Author: GST applicable separately.
Note on D856: Author: GST applicable separately.
Note on D857: Author: GST applicable separately.
Note on D858: Author: GST applicable separately.
Note on D859: Author: GST applicable separately.
Note on D860: Author: GST applicable separately.
Note on D861: Author: GST applicable separately.
Note on D862: Author: GST applicable separately.
Note on D863: Author: GST applicable separately.
Note on D864: Author: GST applicable separately.
Note on D867: Author: GST applicable separately.
Note on D868: Author: GST applicable separately.
Note on D869: Author: GST applicable separately.
Note on D870: Author: GST applicable separately.
Note on D871: Author: GST applicable separately.
Note on D872: Author: GST applicable separately.
Note on D873: Author: GST applicable separately.
Note on D874: Author: GST applicable separately.
Note on D875: Author: GST applicable separately.
Note on D876: Author: GST applicable separately.
Note on D877: Author: GST applicable separately.
Note on D878: Author: GST applicable separately.

## A-1
COST SCHEDULE A-1
| 1 KM OF 33 kV LINE ON PCC POLES / H-BEAMS WITH MAXIMUM SPAN OF 100 METERS USING RACCOON CONDUCTOR | [9 empty] | 2026-27
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4613.69 | 46136.9
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 53.0776 | 255993.1683
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7887.84 | 78878.4
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2564.36 | 25643.6 | 10 | 2564.36 | 25643.6 | 10 | 2564.36 | 25643.6
5 | Back Clamp for Cross Arm
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 10 | 326.97 | 3269.7 |  |  |  | 10 | 326.97 | 3269.7
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 10 | 362.75 | 3627.5
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 426.66 | 4266.6 | 10 | 426.66 | 4266.6 | 10 | 426.66 | 4266.6
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 143.69 | 1436.9 | 10 | 143.69 | 1436.9 | 10 | 143.69 | 1436.9
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 378.54 | 11356.2 | 30 | 378.54 | 11356.2 | 30 | 378.54 | 11356.2
9 | Raccoon ACSR Conductor (80 Sqmm, Al. Eq) with 3% sag | 7130830060 | Mtr | 3100 | 89.5109 | 277483.914 | 3100 | 89.5109 | 277483.914 | 3100 | 89.5109 | 277483.914
10 | Jointing Sleeves suitable ( for 80 Sqmm, Al. Eq. ACSR cond.) | 7130830050 | No | 6 | 51.51 | 309.06 | 6 | 51.51 | 309.06 | 6 | 51.51 | 309.06
11 | (i) Stay set 20 mm | 7130860033 | No | 3 | 1080.47 | 3241.41 | 3 | 1080.47 | 3241.41 | 3 | 1080.47 | 3241.41
| (ii) Stay Clamp For PCC Pole | 7130810193 | Pair | 3 | 326.97 | 980.91 |  |  |  | 3 | 326.97 | 980.91
| (iii) Stay Clamp For "H" Beam | 7130810692 | Pair |  |  |  | 3 | 362.75 | 1088.25
| (iv) Stay Wire 7/8 SWG @ 8.5 kg/ stay | 7130860076 | Kg | 25.5 | 87.2738 | 2225.4824 | 25.5 | 87.2738 | 2225.4824 | 25.5 | 87.2738 | 2225.4824
12 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Rate are inclusive of all T&P and labour charges and GST
13 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 183.37 | 256.718 | 6 | 183.37 | 1100.22 | 1.4 | 183.37 | 256.718
14 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 409.72 | 614.58 | 6 | 409.72 | 2458.32 | 1.5 | 409.72 | 614.58
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 84.3145 | 1686.291 | 20 | 84.3145 | 1686.291 | 20 | 84.3145 | 1686.291
16 | Danger Board | 7130880041 | No | 10 | 101.61 | 1016.1 | 10 | 101.61 | 1016.1 | 10 | 101.61 | 1016.1
17 | Binding wire and tape | 7130830006 | Kg | 3.5 | 221.56 | 775.46 | 3.5 | 221.56 | 775.46 | 3.5 | 221.56 | 775.46
18 | M.S. Nuts and Bolts |  | Kg | 17 |  |  | 17 |  |  | 18
| 16x65 mm | 7130620614 | Kg |  |  |  | 7 | 85.5 | 598.5
| 16x90 mm | 7130620619 | Kg | 3 | 85.5 | 256.5 |  |  |  | 3.5 | 85.5 | 299.25
| 16x140 mm | 7130620625 | Kg |  |  |  | 10 | 84.05 | 840.5
| 16x160 mm | 7130620627 | Kg | 14 | 84.05 | 1176.7 |  |  |  | 14.5 | 84.05 | 1218.725
19 | Guarding 33 kV |  | Rs |  |  | 14047.3161 |  |  | 14047.3161 |  |  | 14047.3161 | Include as per requirement
| (i) G.I. Wire 6 SWG | 7130870045 | Kg | 49 | 69.8234 | 3421.3442 | 49 | 69.8234 | 3421.3442 | 49 | 69.8234 | 3421.3442
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 20 | 69.8234 | 1396.467 | 20 | 69.8234 | 1396.467 | 20 | 69.8234 | 1396.467
| (iii) 33 kV guarding channel | 7130897759 | Set | 1 | 3645.31 | 3645.31 | 1 | 3645.31 | 3645.31 | 1 | 3645.31 | 3645.31
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 362.75 | 1088.25 | 3 | 362.75 | 1088.25 | 3 | 362.75 | 1088.25
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 84.05 | 100.86 | 1.2 | 84.05 | 100.86 | 1.2 | 84.05 | 100.86
| (vi) I--Bolt Big Size | 7130620013 | No | 4 | 155.56 | 622.24 | 4 | 155.56 | 622.24 | 4 | 155.56 | 622.24
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 1080.47 | 2160.94 | 2 | 1080.47 | 2160.94 | 2 | 1080.47 | 2160.94
| (viii) Stay wire 7/8 SWG & 8.5 Kg/stay | 7130860076 | Kg | 17 | 87.2738 | 1483.6549 | 17 | 87.2738 | 1483.6549 | 17 | 87.2738 | 1483.6549
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 85.5 | 128.25 | 1.5 | 85.5 | 128.25 | 1.5 | 85.5 | 128.25
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 402120.3415 |  |  | 632954.7918 |  |  | 449796.6165
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 340779.9504 |  |  | 536402.366 |  |  | 381183.5733
22 | Incidental Charges @ 7.5% on Serial No. 21 : - |  |  |  | 0.075 | 25558.4963 |  | 0.075 | 40230.1774 |  | 0.075 | 28588.768
23 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 472.92 | 4729.2 | 0 | 0 | 0 | 0 | 472.92 | 0
24 | Labour charges as per Schedule No.- AL-1 |  |  |  |  | 57330.56 |  |  | 63919.73 |  |  | 61754.11
25 | Labour charges for concreting |  | Cmt | 2 | 740.31 | 1480.62 | 8 | 740.31 | 5922.48 | 7 | 740.31 | 5182.17
26 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial No. 21 |  |  |  | 0.02 | 6815.599 |  | 0.02 | 10728.0473 |  | 0.02 | 7623.6715
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 21, 22, 23, 24, 25, 26 (i) |  |  |  |  | 54586.8032 |  |  | 82150.3501 |  |  | 60541.5366
28 | Total Estimated Cost excluding GST [Serial no. 21, 22, 23, 24, 25, 26(i), 27] |  |  |  |  | 491281.2289 |  |  | 739353.1508 |  |  | 544873.8294
29 | Applicable CGST @ 9% on Serial no. 28 |  |  |  | 0.09 | 44215.3106 |  | 0.09 | 66541.7836 |  | 0.09 | 49038.6446
30 | Applicable SGST @ 9% on Serial no. 28 |  |  |  | 0.09 | 44215.3106 |  | 0.09 | 66541.7836 |  | 0.09 | 49038.6446
31 | Total Estimated Cost including GST (Serial no. 28+29+30) |  |  |  |  | 579711.8501 |  |  | 872436.718 |  |  | 642951.1187
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 579712 |  |  | 872437 |  |  | 642951
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
3 | All the rates are with considering price variation clause.

## A-2 (A)
COST SCHEDULE A-2 (A)
| 33 KV FOUR POLE STRUCTURE ON PCC / H-BEAM POLE | [5 empty] | 2026-27
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty | PCC Pole 280 kg 9.1 Mtr. Long | H-Beams 37.1 Kg/Mtr., 13 Mtr. Long
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 280 Kg.,9.1 Mtrs. long PCC Poles | 7130800033 | No | 4613.69 | 4 | 18454.76
2 | H-Beams 152 X 152 mm., 37.1 Kg/Mtr 13 Mtr. Long (482.3 Kg x 4 No = 1929.2 Kgs) | 7130601958 | Kg | 53.0776 | 1929.2 |  | 102397.2673
3 | D.C.cross- arm of 100 X 50 X 6 mm. suitable for 5' centre DP | 7130810608 | Set | 5912.78 | 4 | 23651.12 | 23651.12
4 | 33 KV Strain H.W. fitting | 7130820248 | No | 333.97 | 24 | 8015.28 | 8015.28
5 | 33 KV Polymer Disc Insulator | 7130820013 | No | 187.29 | 24 | 4494.96 | 4494.96
6 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 120.4014 | 50 | 6020.0705 | 6020.0705
7 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No. | 378.54 | 8 | 3028.32 | 3028.32
8 | DC cross arm 3.8 Mtr. Channel of 100x50 mm | 7130810006 | Set | 7486.37 | 10 | 74863.7 | 74863.7
9 | (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 326.97 | 16 | 5231.52
| (ii) Stay Clamp For "H" Beam | 7130810692 | Pair | 362.75 | 16 |  | 5804
10 | 33 KV AB Switch | 7131930321 | Each | 23249.28 | 4 | 92997.12 | 92997.12
11 | Concreting of supports @ 0.5 Cmt Per pole for PCC Pole and @ 0.05 Cmt per pole for base padding for PCC pole (1:3:6) | 7130200202 | Cmt. | 2970 | 2.2 | 6534 |  | Rate are inclusive of all T&P and labour charges and GST
| Concreting of supports @ 0.6 Cmt. Per pole for H-Beam and @ 0.05 Cmt per pole for base padding for H-Beam pole (1:3:6) | 7130200202 | Cmt. | 2970 | 2.6 |  | 7722 | Rate are inclusive of all T&P and labour charges and GST
12 | M.S.Angle 75x75x6 mm (for bracing 4 No. @ 60 kg each) | 7130600051 | Kg | 45.5205 | 240 | 10924.9104 | 10924.9104
13 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 143.69 | 4 | 574.76 | 574.76
14 | Red oxide paint | 7130211158 | Ltr | 183.37 | 6 |  | 1100.22
15 | Aluminium paint | 7130210809 | Ltr | 409.72 | 6 |  | 2458.32
16 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 84.3145 | 8 | 674.5164 | 674.5164
17 | Danger Board | 7130880041 | No | 101.61 | 4 | 406.44 | 406.44
18 | Strain Plate (65x8) mm | 7130810624 | No | 101.05 | 12 | 1212.6 | 1212.6
19 | M.S.Nuts and Bolts |  | Kg
| 16x40 mm | 7130620609 | Kg | 86.95 | 2 |  | 173.9
| 16x65 mm | 7130620614 | Kg | 85.5 | 2 |  | 171
| 16x90 mm | 7130620619 | Kg | 85.5 | 10 | 855 | 855
| 16x200 mm | 7130620631 | Kg | 84.05 | 15 | 1260.75 | 1260.75
20 | T-Clamp for Dog Conductor. | 7130830585 | No | 380.53 | 6 | 2283.18 | 2283.18
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 261483.0073 | 351089.4346
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 221595.7689 | 297533.4192 |  | Earlier name was Incidental charges @ 7.5% on Sub Total-1
23 | Incidental Charges @ 7.5% on Serial no. 22 : - |  |  | 0.075 |  | 16619.6827 | 22315.0064
24 | Labour charges for concreting of PCC Pole |  | Cmt | 740.31 | 2.2 | 1628.682
25 | Labour charges for concreting of H-Beam Pole |  | Cmt | 740.31 | 2.6 |  | 1924.806
26 | Labour charges as per Schedule No.- AL-2(A) |  |  |  |  | 19378.52 | 22014.19
27 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 22 |  |  |  | 0.02 | 4431.9154 | 5950.6684
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 22, 23, 24, 25, 26, 27(i) |  |  |  |  | 32956.8211 | 43717.2613
29 | Total Estimated Cost excluding GST [Serial No. 22, 23, 24, 25, 26, 27(i),28] |  |  |  |  | 296611.3901 | 393455.3513
30 | Applicable CGST @ 9% on Serial No 29 |  |  | 0.09 |  | 26695.0251 | 35410.9816
31 | Applicable SGST @ 9% on Serial No 29 |  |  | 0.09 |  | 26695.0251 | 35410.9816
32 | Total Estimated Cost including GST (Serial No 29+30+31) |  |  |  |  | 350001.4403 | 464277.3145
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 350001 | 464277
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.
Note on C19: Author: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole
Note on C20: Author: 2.6 cmt for H-Beam and 2.2 Cmt for PCC Pole
Note on B36: Author: Earlier name was Incidental charges @7.5% on SUB TOTAL-1
Note on B40: Author: Earlier name was - Transportation charges @ 4% Serial No- 22

## A-2 (B)
COST SCHEDULE A-2 (B)
2026-27
33 kV DP STRUCTURE ON PCC POLES / H-BEAM POLE (TO BE SUPPLEMENTED WITH EVERY 1.0 KM OF LINE OF RACCOON / DOG CONDUCTOR)
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg/Mtr 13.0 Mtr long H-Beam |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4613.69 | 9227.38
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 53.0776 | 51198.6337
| (iii) 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 2 | 7887.84 | 15775.68
2 | DC cross arm of 100x50 mm Channel 5' Center | 7130810608 | Set | 1 | 5912.78 | 5912.78 | 1 | 5912.78 | 5912.78 | 1 | 5912.78 | 5912.78
3 | 33 kV Polymer Disc Insulator | 7130820013 | No | 6 | 187.29 | 1123.74 | 6 | 187.29 | 1123.74 | 6 | 187.29 | 1123.74
4 | 33 kV Strain H.W. fitting | 7130820248 | No | 6 | 333.97 | 2003.82 | 6 | 333.97 | 2003.82 | 6 | 333.97 | 2003.82
5 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 378.54 | 1135.62 | 3 | 378.54 | 1135.62 | 3 | 378.54 | 1135.62
6 | Horizontal & cross bracing 5' centre with set of 4 back clamps |  | No | 1 |  |  | 1
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 4 | 326.97 | 1307.88 |  |  |  | 4 | 326.97 | 1307.88
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 362.75 | 1451
| (iii) M.S.Angle 65X65x6 mm | 7130600032 | Kg | 60 | 45.5205 | 2731.2276 | 60 | 45.5205 | 2731.2276 | 60 | 45.5205 | 2731.2276
7 | (i) Stay set 20 mm | 7130860033 | No | 6 | 1080.47 | 6482.82 | 6 | 1080.47 | 6482.82 | 6 | 1080.47 | 6482.82
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair | 6 | 326.97 | 1961.82 |  |  |  | 6 | 326.97 | 1961.82
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 6 | 362.75 | 2176.5
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 51 | 87.2738 | 4450.9648 | 51 | 87.2738 | 4450.9648 | 51 | 87.2738 | 4450.9648
8 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 101.05 | 606.3 | 6 | 101.05 | 606.3 | 6 | 101.05 | 606.3
9 | Concreting @ 0.6 Cmt per pole for H-Beam supports and 0.5 Cmt per pole for 365 kG 11 Mtr. Long PCC @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam (1:3:6) | 7130200202 | Cmt | 2.9 | 2970 | 8613 | 3.1 | 2970 | 9207 | 2.9 | 2970 | 8613 | Rate are inclusive of all T&P and labour charges and GST
10 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 2 | 143.69 | 287.38 | 2 | 143.69 | 287.38 | 2 | 143.69 | 287.38
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 183.37 | 91.685 | 2 | 183.37 | 366.74 | 0.5 | 183.37 | 91.685
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 409.72 | 204.86 | 2 | 409.72 | 819.44 | 0.5 | 409.72 | 204.86
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 84.3145 | 337.2582 | 4 | 84.3145 | 337.2582 | 4 | 84.3145 | 337.2582
14 | Danger Board | 7130880041 | No | 1 | 101.61 | 101.61 | 1 | 101.61 | 101.61 | 1 | 101.61 | 101.61
15 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 86.95 | 43.475 | 0.5 | 86.95 | 43.475 | 0.5 | 86.95 | 43.475
| 16x65 mm | 7130620614 | Kg | 0.5 | 85.5 | 42.75 | 0.5 | 85.5 | 42.75 | 0.5 | 85.5 | 42.75
| 16x90 mm | 7130620619 | Kg |  |  |  | 2.5 | 85.5 | 213.75
| 16x140 mm | 7130620625 | Kg | 2 | 84.05 | 168.1 |  |  |  | 2 | 84.05 | 168.1
| 16x200 mm | 7130620631 | Kg | 4 | 84.05 | 336.2 | 3.5 | 84.05 | 294.175 | 4 | 84.05 | 336.2
16 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 47170.6706 |  |  | 90986.9843 |  |  | 53718.9706
17 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 39975.1446 |  |  | 77107.6138 |  |  | 45524.5514
18 | Incidental Charges @ 7.5% on Serial no. 17 : - |  |  |  | 0.075 | 2998.1358 |  | 0.075 | 5783.071 |  | 0.075 | 3414.3414
19 | Labour charges for concreting |  | Cmt | 2.9 | 740.31 | 2146.899 | 3.1 | 740.31 | 2294.961 | 2.9 | 740.31 | 2146.899
20 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 0 | 472.92 | 0 |  |  |  | 0 | 472.92
21 | Labour charges as per Schedule No.- AL-2 |  |  |  |  | 10572.84 |  |  | 11890.67 |  |  | 11166.07
22 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 17 |  |  |  | 0.02 | 799.5029 |  | 0.02 | 1542.1523 |  | 0.02 | 910.491
23 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 17, 18, 19, 20, 21, 22 (i) |  |  |  |  | 7061.5653 |  |  | 12327.3085 |  |  | 7895.2941
24 | Total Estimated Cost excluding GST [Serial no. 17, 18, 19, 20, 21, 22(i), 23] |  |  |  |  | 63554.0876 |  |  | 110945.7766 |  |  | 71057.6468
25 | Applicable CGST @ 9% on Serial No 24 |  |  |  | 0.09 | 5719.8679 |  | 0.09 | 9985.1199 |  | 0.09 | 6395.1882
26 | Applicable SGST @ 9% on Serial No 24 |  |  |  | 0.09 | 5719.8679 |  | 0.09 | 9985.1199 |  | 0.09 | 6395.1882
27 | Total Estimated Cost including GST (Serial No 24+25+26) |  |  |  |  | 74993.8234 |  |  | 130916.0164 |  |  | 83848.0233
28 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 74994 |  |  | 130916 |  |  | 83848
Note:
1 | This Schedule is to be supplemented with Schedule A-1 & A-3.
2 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
3 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
4 | All the rates are with considering price variation clause.

## A-3
COST SCHEDULE - A-3
1 KM OF 33 kV LINE ON PCC POLES / H-BEAM SUPPORT WITH MAXIMUM SPAN OF 100 METERS USING DOG CONDUCTOR
2026-27
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | "H" Beam 152x152 mm 37.1 Kg/Mtr 13.0 Mtr |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 10 | 4613.69 | 46136.9
2 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30Kg) x 10 No = 4823 Kgs | 7130601958 | Kg |  |  |  | 4823 | 53.0776 | 255993.1683
3 | 365 Kg; 11 Mtr long PCC Pole | 7130800002 | No | [6 empty] | 10 | 7887.84 | 78878.4
4 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 10 | 2564.36 | 25643.6 | 10 | 2564.36 | 25643.6 | 10 | 2564.36 | 25643.6
5 | Back Clamp for Cross Arm
| (i) Stay Clamp For PCC Pole | 7130810193 | Pair | 10 | 326.97 | 3269.7 |  |  |  | 10 | 326.97 | 3269.7
| (ii) Stay Clamp For H-Beam Pole | 7130810692 | Pair |  |  |  | 10 | 362.75 | 3627.5
6 | 33 kV Top Clamps | 7130810676 | No | 10 | 426.66 | 4266.6 | 10 | 426.66 | 4266.6 | 10 | 426.66 | 4266.6
7 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 10 | 143.69 | 1436.9 | 10 | 143.69 | 1436.9 | 10 | 143.69 | 1436.9
8 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 30 | 378.54 | 11356.2 | 30 | 378.54 | 11356.2 | 30 | 378.54 | 11356.2
9 | DOG ACSR Conductor (100 Sqmm, Al. Eq) with 3% sag | 7130830063 | Mtr | 3100 | 120.4014 | 373244.371 | 3100 | 120.4014 | 373244.371 | 3100 | 120.4014 | 373244.371
10 | Jointing Sleeves (suitable for 100 Sqmm, Al. Eq. ACSR cond.) | 7130830051 | No | 6 | 201.06 | 1206.36 | 6 | 201.06 | 1206.36 | 6 | 201.06 | 1206.36
11 | Stay set 20 mm | 7130860033 | No | 3 | 1080.47 | 3241.41 | 3 | 1080.47 | 3241.41 | 3 | 1080.47 | 3241.41
12 | Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | Pair | 3 | 326.97 | 980.91 |  |  |  | 3 | 326.97 | 980.91
| (ii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 3 | 362.75 | 1088.25
13 | Stay Wire 7/8 SWG @ 8.5 kg Per stay | 7130860076 | Kg | 25.5 | 87.2738 | 2225.4824 | 25.5 | 87.2738 | 2225.4824 | 25.5 | 87.2738 | 2225.4824
14 | Concreting of H-Beam supports @ 0.6 cmt. Per pole and @ 0.3 Cmt per stay and @ 0.05 cmt per pole for base padding for PCC / H- Beam pole (1:3:6) | 7130200202 | Cmt | 2 | 2970 | 5940 | 8 | 2970 | 23760 | 7 | 2970 | 20790 | Rate are inclusive of all T&P and labour charges and GST
15 | Red Oxide Paint | 7130211158 | Ltr | 1.4 | 183.37 | 256.718 | 6 | 183.37 | 1100.22 | 1.4 | 183.37 | 256.718
16 | Aluminium Paint | 7130210809 | Ltr | 1.5 | 409.72 | 614.58 | 6 | 409.72 | 2458.32 | 1.5 | 409.72 | 614.58
17 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 20 | 84.3145 | 1686.291 | 20 | 84.3145 | 1686.291 | 20 | 84.3145 | 1686.291
18 | Danger Boards | 7130880041 | No | 10 | 101.61 | 1016.1 | 10 | 101.61 | 1016.1 | 10 | 101.61 | 1016.1
19 | Binding wire and tape | 7130830006 | Kg | 3.5 | 221.56 | 775.46 | 3.5 | 221.56 | 775.46 | 3.5 | 221.56 | 775.46
20 | M.S. Nuts and Bolts |  | Kg | 18 |  |  | 18 |  |  | 18
| 16x40 mm | 7130620609 | Kg |  |  |  | 0.5 | 86.95 | 43.475
| 16x65 mm | 7130620614 | Kg |  |  |  | 7.5 | 85.5 | 641.25
| 16x90 mm | 7130620619 | Kg | 3.5 | 85.5 | 299.25 |  | 85.5 |  | 3.5 | 85.5 | 299.25
| 16x140 mm | 7130620625 | Kg |  |  |  | 10 | 84.05 | 840.5
| 16x160 mm | 7130620627 | Kg | 14.5 | 84.05 | 1218.725 |  | 84.05 |  | 14.5 | 84.05 | 1218.725
21 | Guarding | [11 empty] | Include as per requirement
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 69.8234 | 3421.3442 | 49 | 69.8234 | 3421.3442 | 49 | 69.8234 | 3421.3442
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 69.8234 | 1396.467 | 20 | 69.8234 | 1396.467 | 20 | 69.8234 | 1396.467
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 1 | 3645.31 | 3645.31 | 1 | 3645.31 | 3645.31 | 1 | 3645.31 | 3645.31
| (iv) Stay Clamp Set | 7130810692 | Pair | 3 | 362.75 | 1088.25 | 3 | 362.75 | 1088.25 | 3 | 362.75 | 1088.25
| (v) M.S. Nut & Bolt 16x140 mm | 7130620625 | Kg | 1.2 | 84.05 | 100.86 | 1.2 | 84.05 | 100.86 | 1.2 | 84.05 | 100.86
| (vi) I-Bolt Big Size | 7130620013 | No | 4 | 155.56 | 622.24 | 4 | 155.56 | 622.24 | 4 | 155.56 | 622.24
| (vii) Stay set 20 mm complete | 7130860033 | No | 2 | 1080.47 | 2160.94 | 2 | 1080.47 | 2160.94 | 2 | 1080.47 | 2160.94
| (viii) Stay wire 7/8 SWG & 8.5 Kg/ stay | 7130860076 | Kg | 17 | 87.2738 | 1483.6549 | 17 | 87.2738 | 1483.6549 | 17 | 87.2738 | 1483.6549
| (ix) M.S.Nuts & Bolts 16x90 mm. | 7130620619 | Kg | 1.5 | 85.5 | 128.25 | 1.5 | 85.5 | 128.25 | 1.5 | 85.5 | 128.25
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 498862.8735 |  |  | 729698.7738 |  |  | 546454.3735
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 422765.147 |  |  | 618388.7914 |  |  | 463096.9267
24 | Incidental Charges @ 7.5% on Serial no. 23 : - |  |  |  | 0.075 | 31707.386 |  | 0.075 | 46379.1594 |  | 0.075 | 34732.2695
25 | Labour charges for concreting |  | Cmt | 2 | 740.31 | 1480.62 | 8 | 740.31 | 5922.48 | 7 | 740.31 | 5182.17
26 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 10 | 472.92 | 4729.2 |  |  |  | 0 | 472.92
27 | Labour charges as per Schedule No.- AL-3 |  |  |  |  | 59873.34 |  |  | 66462.51 |  |  | 64296.89
28 | Transportation charges of all line materials:-
(i) | Upto 100 km @ 2% on Serial no. 23 |  |  |  | 0.02 | 8455.3029 |  | 0.02 | 12367.7758 |  | 0.02 | 9261.9385
29 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 23, 24, 25, 26, 27 ,28(i) |  |  |  |  | 66126.3745 |  |  | 93690.0896 |  |  | 72071.2743
30 | Total Estimated Cost excluding GST [Serial no. 23, 24, 25, 26, 27, 28(i), 29] |  |  |  |  | 595137.3705 |  |  | 843210.8061 |  |  | 648641.4691
31 | Applicable CGST @ 9% on Serial No 30 |  |  |  | 0.09 | 53562.3633 |  | 0.09 | 75888.9726 |  | 0.09 | 58377.7322
32 | Applicable SGST @ 9% on Serial No 30 |  |  |  | 0.09 | 53562.3633 |  | 0.09 | 75888.9726 |  | 0.09 | 58377.7322
33 | Total Estimated Cost including GST (Serial No 30+31+32) |  |  |  |  | 702262.0972 |  |  | 994988.7512 |  |  | 765396.9335
34 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 702262 |  |  | 994989 |  |  | 765397
Note:
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
3 | All the rates are with considering price variation clause.

## A-3 (A)
COST SCHEDULE -- A-3 (A)
2026-27
SCHEDULE FOR AUGMENTATION OF 1 kM OF 33 kV LINE FROM RACCOON TO DOG CONDUCTOR
S.No. | Particulars | New SAP Bin Code | Unit | Qty | Cost per Unit | Cost
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | ACSR Dog Conductor 100 sq.mm | 7130830063 | Km | 3.1 | 120401.41 | 373244.371
2 | Jointing Sleeves suitable for Dog ACSR Conductor | 7130830051 | No | 6 | 201.06 | 1206.36
3 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 6 | 378.54 | 2271.24
4 | Guarding | [5 empty] | Include as per requirement
| (i) GI Wire 6 SWG | 7130870045 | Kg | 49 | 69.8234 | 3421.3442
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 20 | 69.8234 | 1396.467
| (iii) 33 kV Guarding Channel (Set) | 7130897759 | Set | 1 | 3645.31 | 3645.31
| (iv) M.S Nut & Bolt 16x140 mm. | 7130620625 | Kg | 1.2 | 84.05 | 100.86
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 155.56 | 622.24
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 1080.47 | 2160.94
| (vii) Stay Wire 7/8 SWG @ 8.5 Kg. Stay | 7130860076 | Kg | 17 | 87.2738 | 1483.6549
| (viii) MS Nut & Bolt 16x90 mm | 7130620619 | Kg | 1.5 | 85.5 | 128.25
5 | Concreting of Stay Set @ 0.3 Cmt per stay (1:3:6) | 7130200202 | Cmt | 0.6 | 2970 | 1782 | Rate are inclusive of all T&P and labour charges and GST
6 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 391463.0371
7 | Material cost excluding GST ( Sub Total-1/1.18 ) |  |  |  |  | 331748.3365
8 | Incidental Charges @ 7.5 % on Serial no. 7 : - |  |  |  | 0.075 | 24881.1252
9 | Labour charges for concreting |  | Cmt | 0.6 | 740.31 | 444.186
10 | Labour charges including dismantling & stringing of line for Dog conductor as per Sch No. AL-3(A) |  |  |  |  | 35073.36
11 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 7 |  |  |  | 0.02 | 6634.9667
12 | Transportation charges of scrap Raccoon conductor from site to Area Store |  |  |  | 0.02 | 2351.5586
13 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 7, 8, 9,10,11(i), 12 |  |  |  |  | 50141.6916
14 | Total Estimated Cost excluding GST (Row 7, 8, 9, 10, 11(i), 12, 13) |  |  |  |  | 451275.2247
15 | Applicable CGST @ 9% on Serial No 14 |  |  |  | 0.09 | 40614.7702
16 | Applicable SGST @ 9% on Serial No 14 |  |  |  | 0.09 | 40614.7702
17 | Returnable cost of old Raccoon conductor (cost in 2004-05) assuming 25 years of life & 20 years in service |  |  | 3.1 | 10253.16 | 31784.796
18 | Total Estimated Cost including GST (Serial No 14+15+16-17) |  |  |  |  | 500719.9692
19 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 500720
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.
Note on B28: Author: Name changed. Earlier name was - Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 6, 8, 9, 10, 11, 12

## A-3 (B)
COST SCHEDULE -- A-3 (B)
2026-27
COST SCHEDULE FOR ADDITIONAL (MID SPAN) POLE FOR 33 kV LINE USING 37.1 KG / MTR 13 M. LONG H-BEAM SUPPORT
S. No. | PARTICULARS | New SAP Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) H-Beam
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 482.3 | 53.0776 | 25599.3168
2 | 33 kV "V" Cross arm 75x75x6 mm | 7130810595 | No | 1 | 2564.36 | 2564.36
3 | Cross Arm Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 1 | 362.75 | 362.75
4 | 33 kV Top Clamp | 7130810676 | No | 1 | 426.66 | 426.66
5 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | Each | 1 | 143.69 | 143.69
6 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 378.54 | 1135.62
7 | Concreting of H-Beam support @ 0.6 Cmt. per pole and @ 0.05 Cmt per pole for base padding of H-Beam pole (1:3:6). | 7130200202 | Cmt | 0.65 | 2970 | 1930.5 | Rate are inclusive of all T&P and labour charges and GST
8 | Red Oxide Paint | 7130211158 | Ltr | 1 | 183.37 | 183.37
9 | Aluminium Paint | 7130210809 | Ltr | 1 | 409.72 | 409.72
10 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 2 | 84.3145 | 168.6291
11 | Danger Boards | 7130880041 | No | 1 | 101.61 | 101.61
12 | Binding wire and tape | 7130830006 | Kg | 0.5 | 221.56 | 110.78
13 | M.S. Nuts and Bolts |  | Kg | 2.5
| 16x40 mm | 7130620609 | Kg | 0.5 | 86.95 | 43.475
| 16x65 mm | 7130620614 | Kg | 1 | 85.5 | 85.5
| 16x90 mm | 7130620619 | Kg
| 16x140 mm | 7130620625 | Kg | 1 | 84.05 | 84.05
| 16x160 mm | 7130620627 | Kg
14 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 33350.0309
15 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 28262.7381
16 | Incidental Charges @ 7.5% on Serial no.15 : - |  |  |  | 0.075 | 2119.7054
17 | Labour charges for concreting |  | Cmt | 0.65 | 740.31 | 481.2015
18 | Labour charges as per Schedule No.- AL-3 (B) |  |  |  |  | 3956.78
19 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 15 |  |  |  | 0.02 | 565.2548
20 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 15, 16, 17,18, 19(i) |  |  |  |  | 4423.21
21 | Total Estimated Cost excluding GST (Serial No 15, 16, 17, 18, 19(i), 20) |  |  |  |  | 39808.8897
22 | Applicable CGST @ 9% on Serial No 21 |  |  |  | 0.09 | 3582.8001
23 | Applicable SGST @ 9% on Serial No 21 |  |  |  | 0.09 | 3582.8001
24 | Total Estimated Cost including GST (Serial No 21+22+23) |  |  |  |  | 46974.4898
25 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 46974
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.

## A-4
COST SCHEDULE A-4
1 KM OF 33 kV LINE ON 37.1 KG / MTR 13 M. LONG H-BEAM SUSPENSION TYPE WITH PANTHER CONDUCTOR (WITH MAXIMUM SPAN OF 50 METERS)
2026-27
S. No. | PARTICULARS | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M long (482.30 Kg) x 20 No = 9646 Kgs | 7130601958 | Kg | 9646 | 53.0776 | 511986.3367
2 | DC Cross arm (100x50 mm) Channel 2.4 Mtr. (1.5 X 20 = 30) | 7130810512 | Set | 30 | 4332.59 | 129977.7
3 | 33 kV Suspension Hardware suitable for Panther Conductor (3x20=60) | 7130820312 | Set | 60 | 2861.66 | 171699.6
4 | 33 kV Polymer Disc Insulator (9x20=180) | 7130820013 | No. | 60 | 187.29 | 11237.4
5 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 20 | 143.69 | 2873.8
6 | ACSR Panther Conductor with 5% sag | 7130830070 | Mtr. | 3150 | 266.8655 | 840626.3565
7 | Jointing Sleeves suitable for Panther conductor | 7130830971 | No. | 6 | 310.74 | 1864.44
8 | Stay Set 20 mm Complete | 7130860033 | Set. | 12 | 1080.47 | 12965.64
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 100 | 362.75 | 36275
10 | Stay Wire 7/8 SWG @ 8.5 Kg/Stay | 7130860076 | Kg. | 170 | 87.2738 | 14836.5494
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt. per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 17.2 | 2970 | 51084 | Rate are inclusive of all T&P and labour charges and GST
12 | Red Oxide Paint | 7130211158 | Ltr. | 26 | 183.37 | 4767.62
13 | Aluminium Paint | 7130210809 | Ltr. | 26 | 409.72 | 10652.72
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg. | 40 | 84.3145 | 3372.582
15 | Danger Boards | 7130880041 | No. | 20 | 101.61 | 2032.2
16 | Binding Wire & Tape | 7130830006 | Kg. | 8 | 221.56 | 1772.48
17 | MS Nut & Bolts |  | Kg. | 123
| 16x40 mm | 7130620609 | Kg. | 2 | 86.95 | 173.9
| 16x65 mm | 7130620614 | Kg. | 30 | 85.5 | 2565
| 16x90 mm | 7130620619 | Kg. | 20 | 85.5 | 1710
| 16x140 mm | 7130620625 | Kg.
| 16x160 mm | 7130620627 | Kg. | 1 | 84.05 | 84.05
| 16x200 mm | 7130620631 | Kg.
| 16x250 mm | 7130620637 | Kg. | 70 | 84.05 | 5883.5
18 | MS Angle 65x65x6 for Tie | 7130600032 | Kg. | 435 | 45.5205 | 19801.4001
19 | Strain Plate (65x8 mm) | 7130810624 | No. | 120 | 101.05 | 12126
20 | Guarding 33 kV for single span | [5 empty] | Include as per requirement
| (i) G.I. Wire 6 SWG | 7130870045 | Kg. | 40 | 69.8234 | 2792.934
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg. | 20 | 69.8234 | 1396.467
| (iii) 33 kV Guarding Channel | 7130897759 | Set | 2 | 3645.31 | 7290.62
| (iv) M.S Nut & Bolt 16x250 mm. | 7130620637 | Kg. | 5 | 84.05 | 420.25
| (v) I - Bolt Big Size | 7130620013 | No | 4 | 155.56 | 622.24
| (vi) Stay Set 20 mm Complete | 7130860033 | No | 2 | 1080.47 | 2160.94
| (vii) Stay Wire 7/8 SWG & 8.5 Kg. Stay | 7130860076 | Kg. | 17 | 87.2738 | 1483.6549
| (viii) Stay Clamp for "H" Beam | 7130810692 | Pair | 2 | 362.75 | 725.5
| (ix) MS Nut & Bolt 16x90 mm | 7130620619 | Kg. | 1 | 85.5 | 85.5
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1867346.3806
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1582496.9327
23 | Incidental Charges @ 7.5% on Serial no. 22 : - |  |  |  | 0.075 | 118687.27
24 | Labour charges for concreting |  | Cmt | 17.2 | 740.31 | 12733.332
25 | Labour Charges per Km as per Schedule - AL-4 |  | Km | 1 |  | 163486.65
26 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 22 |  |  |  | 0.02 | 31649.9387
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 22, 23, 24, 25, 26(i) |  |  |  |  | 238631.7654
28 | Total Estimated Cost excluding GST (Serial No 22, 23, 24, 25, 26(i), 27) |  |  |  |  | 2147685.8888
29 | Applicable CGST @ 9% on Serial No 28 |  |  |  | 0.09 | 193291.73
30 | Applicable SGST @ 9% on Serial No 28 |  |  |  | 0.09 | 193291.73
31 | Total Estimated Cost including GST (Serial No 28+29+30) |  |  |  |  | 2534269.3487
32 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2534269
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
3 | All the rates are with considering price variation clause.

## A-5
COST SCHEDULE A-5
33 KV D.P. STRUCTURE ON 13 M. LONG H-BEAM POLE FOR PANTHER CONDUCTOR (TO BE SUPPLEMENTED WITH EVERY 0.3 KM OF SUSPENSION LINE)
2026-27
S. No. | Particulars | New Sap Bin Code | Unit | 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg. | 964.6 | 53.0776 | 51198.6337
2 | DC Cross arm (100x50 mm) Channel 5' Center | 7130810608 | Set | 1 | 5912.78 | 5912.78
3 | 33 kV Tension Hardware suitable for Panther Conductor | 7130870318 | Set | 6 | 1315.11 | 7890.66
4 | 33 kV Suspension Hardware suitable for Panther Conductor | 7130820312 | Set | 3 | 2861.66 | 8584.98
5 | 33 kV Polymer Disc Insulator | 7130820013 | No. | 9 | 187.29 | 1685.61
6 | Earthing Set (Coil Earth as per Drg. No. G/007) | 7130870013 | No. | 2 | 143.69 | 287.38
7 | Horizontal & Cross bracing |  | No. | 1
| (i) Stay Clamp for "H" Beam | 7130810692 | Pair | 4 | 362.75 | 1451
| (ii) M.S. Angle 65X65x6 mm | 7130600032 | Kg | 60 | 45.5205 | 2731.2276
8 | Stay Set 20 mm complete | 7130860033 | Set. | 6 | 1080.47 | 6482.82
9 | Stay Clamp for "H" Beam | 7130810692 | Pair | 9 | 362.75 | 3264.75
10 | Stay Wire 7/8 SWG @ 8.5 Kg./pole | 7130860076 | Kg. | 51 | 87.2738 | 4450.9648
11 | Concreting of H-Beam Supports @ 0.6 Cmt. Per Pole; @ 0.05 Cmt per Pole for base Padding & @ 0.3 Cmt. Per stay (1:3:6) | 7130200202 | Cmt. | 3.1 | 2970 | 9207 | Rate are inclusive of all T&P and labour charges and GST
12 | Red Oxide Paint | 7130211158 | Ltr. | 2 | 183.37 | 366.74
13 | Aluminium Paint | 7130210809 | Ltr. | 2 | 409.72 | 819.44
14 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 84.3145 | 337.2582
15 | Danger Board | 7130880041 | No | 2 | 101.61 | 203.22
16 | Strain Plate (65x8 mm) | 7130810624 | No. | 6 | 101.05 | 606.3
17 | MS Nut & Bolts |  | Kg. | 15
| 16x40 mm | 7130620609 | Kg. | 1 | 86.95 | 86.95
| 16x65 mm | 7130620614 | Kg. | 3 | 85.5 | 256.5
| 16x90 mm | 7130620619 | Kg. | 1 | 85.5 | 85.5
| 16x140 mm | 7130620625 | Kg. | 2 | 84.05 | 168.1
| 16x160 mm | 7130620627 | Kg. | 2 | 84.05 | 168.1
| 16x200 mm | 7130620631 | Kg. | 2 | 84.05 | 168.1
| 16x250 mm | 7130620637 | Kg. | 4 | 84.05 | 336.2
18 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 106750.2143
19 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 90466.2833
20 | Incidental Charges @ 7.5% on Serial no. 19 : - |  |  |  | 0.075 | 6784.9712
21 | Labour charges for concreting |  | Cmt | 3.1 | 740.31 | 2294.961
22 | Labour Charges as per Schedule AL-2 |  |  |  |  | 11890.67
23 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 19 |  |  |  | 0.02 | 1809.3257
24 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 19, 20, 21, 22, 23(i), |  |  |  |  | 14155.7764
25 | Total Estimated Cost excluding GST (Serial No 19, 20, 21, 22, 23(i), 24) |  |  |  |  | 127401.9876
26 | Applicable CGST @ 9% on Serial No 25 |  |  |  | 0.09 | 11466.1789
27 | Applicable SGST @ 9% on Serial No 25 |  |  |  | 0.09 | 11466.1789
28 | Total Estimated Cost including GST (Serial No 25+26+27) |  |  |  |  | 150334.3454
29 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 150334
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.

## A-6
COST SCHEDULE A-6
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG RAIL / ROAD CORRIDOR / ROUTE LENGTH OF G.I. PIPE/HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2026-27
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique (for Railway works) on 3x400 sq.mm AB XLPE Cable | Using HDD Technique (for Road crossing works) on 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | G.l. Pipe 150 mm OD (Class B as per railway) | 7130641035 | Mtr | 1487.06 | 120 | 178447.2
2 | HDPE pipe of size 160 mm OD/140 mm ID PN 10 PE 100 HDR | 7132461804 | Mtr | 1294.34 | 120 |  | 155320.8
3 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 560.41 | 20 |  | 11208.2
4 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 3202.9493 | 190 | 608560.3613 | 608560.3613
5 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 45866.77 | 4 | 183467.08 | 183467.08
6 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1106.27 | 24 | 26550.48 | 26550.48
7 | Back Clamp Rail for H-Beam | 7130810361 | Pair | 347.95 | 5 | 1739.75 | 1739.75
8 | M.S.Channel 100x50 mm | 7130600230 | kg | 45.5205 | 30 | 1365.6138 | 1365.6138
9 | Caping of G.I. Pipe/HDPE Pipe on both ends using end caps and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000
10 | M.S.Flat (50x6) mm | 7130600173 | kg | 51.0754 | 100 | 5107.541 | 5107.541
11 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224
12 | Sand | 7132498006 | Cmt | 737.1 | 1.2 | 884.52 | 884.52
13 | 33 kV Porcelain Lightning Arrestors | 7130840021 | Each | 4289.09 | 6 | 25734.54 | 25734.54
14 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 89.5109 | 18 | 1611.1969 | 1611.1969
15 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 380.53 | 6 | 2283.18 | 2283.18
16 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No. | 870.41 | 10 | 8704.1 | 8704.1
17 | T-clamp for lightning arrestor | 7130830586 | No. | 304.09 | 6 | 1824.54 | 1824.54
18 | Bi-metallic clamp for earthing | 7130830603 | No. | 459.86 | 4 | 1839.44 | 1839.44
19 | Bhatta bricks for manufacturing of 2 Nos. chambers at both end | 7132498054 | No. | 6.57 | 128 | 840.96 | 840.96
20 | Cement | 7130200401 | Bags | 354 | 2 | 708 | 708
21 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway authorities including liaisoning work etc. |  | LS | LS | LS | 25000
22 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1082892.503 | 1045974.303
23 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 917705.511 | 886418.9009
24 | Incidental Charges @ 7.5% on Serial no. 23 : - |  |  | 0.075 |  | 68827.9133 | 66481.4176
25 | Service in lieu of Earthing Coal & Sand etc |  | No | 3361.28 | 10 | 33612.8 | 33612.8
26 | Labour Charges (using HDD Technique **) as per Schedule AL-5 |  |  |  |  | 411735.62 | 319903.22
27 | Labour Charges for excavation of cable trench beyond the length of G.I. Pipe/HDPE Pipe upto DP Structure & for manufacturing of chamber |  | CMT | 324.98 | 12.432 | 4040.1514 | 4040.1514
28 | Supervision charges @ 15% Serial no. 23, 26, 27 |  |  |  | 0.15 | 200022.1924 | 181554.3408
29 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 23 |  |  |  | 0.02 | 18354.1102 | 17728.378
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 23, 24, 25,26,27, 29(i) |  |  |  |  | 181784.5132 | 166023.1085
31 | Total Estimated Cost excluding GST (Serial No 23, 24, 25, 26,27,28,29(i), 30) |  |  |  |  | 1836082.8115 | 1675762.3171
32 | Applicable CGST @ 9% on Serial No 31 |  |  | 0.09 |  | 165247.453 | 150818.6085
33 | Applicable SGST @ 9% on Serial No 31 |  |  | 0.09 |  | 165247.453 | 150818.6085
34 | Charges payable to Railway as per actual demand note (Way leave charge) OR Municipality Charges payable to Local bodies as per Demand note | LS | LS | LS | LS | 250000 | 250000
35 | Power block charges (As per requirement of railway- if applicable) | LS | LS | LS | LS | 150000
36 | Total Estimated Cost including GST [for Col. 07 = Serial No 31+32+33+34+35] & [for Col. 08 = Serial No 31+32+33+34] |  |  |  |  | 2416577.7176 | 2227399.5342
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2416578 | 2227400
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
This schedule is prepared for 60 Mtr Corridor of Railway / Road crossing. Estimate may be framed as per actual site conditions and actual width of the rail / road corridor.
*** | The way leave charges/power block charges/other charges payable for obtaining railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.
3 | The Estimate should be prepared including spare cable when proposed feeder laying radial
*
***
Fill appropriate cost
Fill appropriate cost
Fill appropriate cost
Note on G35: 89326879: ***
Note on G44: Author: Fill appropriate cost (LS amt. 250000.00 taken for calculation)
Note on H44: Author: Fill appropriate cost (LS amt. 250000.00 taken for calculation)
Note on G45: Author: Fill appropriate cost (LS amt. 1500000.00 taken for calculation)
Note on H45: Author: Fill appropriate cost (LS amt. 1500000.00 taken for calculation)

## A-7
COST SCHEDULE A-7
SCHEDULE FOR LAST SPAN CABLING OF 33 KV H.T. CONNECTION
2026-27
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 3x185 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 53.0776 | 482.3 | 25599.3168 | 25599.3168
2 | 3x185 sq.mm 33 kV AB XLPE Cable | 7130310053 | Mtr. | 1924.2985 | 50 | 96214.926
3 | 3x240 sq.mm 33 kV AB XLPE Cable | 7130310054 | Mtr. | 2446.9444 | 50 |  | 122347.2205
4 | 33 kV Termination Kit for 3x185 sqmm AB XLPE Cable * | 7130320039 | Set | 20534.75 | 2 | 41069.5
5 | 33 kV Termination Kit for 3x240 sqmm AB XLPE Cable * | 7130320040 | Set | 23957.22 | 2 |  | 47914.44
6 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 143.69 | 1 | 143.69 | 143.69
7 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3548.55 | 2 | 7097.1 | 7097.1
8 | Stay Set 20 mm | 7130860033 | No | 1080.47 | 2 | 2160.94 | 2160.94
9 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 87.2738 | 17 | 1483.6549 | 1483.6549
10 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2970 | 1.25 | 3712.5 | 3712.5 | Rate are inclusive of all T&P and labour charges and GST
11 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 1 | 183.37 | 183.37
12 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 1 | 409.72 | 409.72
13 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 84.3145 | 2 | 168.6291 | 168.6291
14 | Danger Board | 7130880041 | No | 101.61 | 1 | 101.61 | 101.61
15 | Stay Clamp for "H" Beam | 7130810692 | Pair | 362.75 | 4 | 1451 | 1451
16 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 86.95 | 5 | 434.75 | 434.75
17 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 85.5 | 1 | 85.5 | 85.5
18 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 1163.86 | 2 | 2327.72 | 2327.72
19 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 870.41 | 2 | 1740.82 | 1740.82
20 | Cable tie for AB Cable | 7130320045 | No | 34.57 | 25 | 864.25 | 864.25
21 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 185248.9969 | 218226.2314
22 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 156990.6753 | 184937.4842
23 | Incidental Charges @ 7.5% on Serial no. 22 : - |  |  | 0.075 |  | 11774.3006 | 13870.3113
24 | Labour Charges AL-7 |  |  | 24835 | 1 | 24835 | 24835
25 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 22 |  |  |  | 0.02 | 3139.8135 | 3698.7497
26 | Labour charges for concreting |  | Cmt | 740.31 | 1.25 | 925.3875 | 925.3875
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 3361.28 | 2 | 6722.56 | 6722.56
28 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 22, 23, 24, 25(i), 26, 27 |  |  |  |  | 25548.4671 | 29373.6866
29 | Total Estimated Cost excluding GST (Serial No 22, 23, 24, 25(i), 26, 27, 28) |  |  |  |  | 229936.2041 | 264363.1793
30 | Applicable CGST @ 9% on Serial No 29 |  |  | 0.09 |  | 20694.2584 | 23792.6861
31 | Applicable SGST @ 9% on Serial No 29 |  |  | 0.09 |  | 20694.2584 | 23792.6861
32 | Total Estimated Cost including GST (Serial No 29+30+31) |  |  |  |  | 271324.7208 | 311948.5516
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 271325 | 311949
* | Note -- Appropriate size of termination kit and 33 kV AB XLPE Cable may be used for S.No 04 and 05 acccording to the load of HT connection.
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.

## A-8
COST SCHEDULE A-8
33 KV MEDP STRUCTURE ON PCC POLE / H-BEAM POLE (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2026-27
S No | PARTICULARS | New SAP Bin Code | Unit | 280 Kg; 9.1 Mtr long PCC Pole |  |  | 37.1 Kg / Mtr 13.0 Mtr long H-Beam
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | (i) 280 Kg; 9.1 Mtr long PCC Pole | 7130800033 | No | 2 | 4613.69 | 9227.38
| (ii) H-Beam 152x152 mm 37.1 Kg/Mtr; 13 Mtr long (482.3 Kg) / pole x 2 No = 964.6 Kgs | 7130601958 | Kg |  |  |  | 964.6 | 53.0776 | 51198.6337
2 | DC cross arm of 100x50 mm Channel (3.8 Mtr. Long) | 7130810608 | Set | 2 | 5912.78 | 11825.56 | 2 | 5912.78 | 11825.56
3 | 33 KV Polymer Disc Insulator | 7130820013 | Each | 6 | 187.29 | 1123.74 | 6 | 187.29 | 1123.74
4 | 33 KV Strain H.W. fitting | 7130820248 | No | 6 | 333.97 | 2003.82 | 6 | 333.97 | 2003.82
5 | 33 KV Polymeric Pin insulator with Pin | 7130820009 | No | 3 | 378.54 | 1135.62 | 3 | 378.54 | 1135.62
6 | PCC Pole Clamp for fixing of Channels | 7130810193 | Pair | 4 | 326.97 | 1307.88
7 | H-Beam pole clamp for fixing of channel | 7130810692 | Pair |  |  |  | 4 | 362.75 | 1451
8 | (i) Stay set 20 mm | 7130860033 | No | 4 | 1080.47 | 4321.88 | 4 | 1080.47 | 4321.88
| (ii) Stay Clamp for PCC Pole | 7130810193 | Pair | 4 | 326.97 | 1307.88
| (iii) Stay Clamp for "H" Beam | 7130810692 | Pair |  |  |  | 4 | 362.75 | 1451
| (iv) Stay Wire 7/8 SWG @ 8.5 kg Per Pole | 7130860076 | Kg | 34 | 87.2738 | 2967.3099 | 34 | 87.2738 | 2967.3099
9 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 6 | 101.05 | 606.3 | 6 | 101.05 | 606.3
10 | Concreting of H-Beam supports @ 0.6 Cmt per pole ; @0.5 Cmt. Per 280 kG PCC Pole, @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole (1:3:6) | 7130200202 | Cmt | 2.3 | 2970 | 6831 | 2.5 | 2970 | 7425 | Rate are inclusive of all T&P and labour charges and GST
11 | Earthing Set (Coil earth as per Drg. No. g/007) | 7130870013 | No | 2 | 143.69 | 287.38 | 2 | 143.69 | 287.38
12 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 183.37 | 91.685 | 2 | 183.37 | 366.74
13 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 409.72 | 204.86 | 2 | 409.72 | 819.44
14 | Barbed wire (@ 2 Kg/Pole) | 7130610206 | Kg | 4 | 84.3145 | 337.2582 | 4 | 84.3145 | 337.2582
15 | Danger Board | 7130880041 | No | 1 | 101.61 | 101.61 | 1 | 101.61 | 101.61
16 | M.S. Nuts and Bolts |  | Kg | 7 |  |  | 7
| 16x40 mm | 7130620609 | Kg | 0.5 | 86.95 | 43.475 | 0.5 | 86.95 | 43.475
| 16x65 mm | 7130620614 | Kg | 0.5 | 85.5 | 42.75 | 0.5 | 85.5 | 42.75
| 16x90 mm | 7130620619 | Kg |  |  |  | 2.5 | 85.5 | 213.75
| 16x140 mm | 7130620625 | Kg | 2 | 84.05 | 168.1
| 16x200 mm | 7130620631 | Kg | 4 | 84.05 | 336.2 | 3.5 | 84.05 | 294.175
17 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 2 | 870.41 | 1740.82 | 2 | 870.41 | 1740.82
18 | G.I.Bend of 40 mm dia. | 7130640171 | Each | 2 | 106.78 | 213.56 | 2 | 106.78 | 213.56
19 | 33 KV Porcelain Lightning Arrestors | 7130840021 | Each | 3 | 4289.09 | 12867.27 | 3 | 4289.09 | 12867.27
20 | 33 KV CTPT unit of appropriate capacity |  | No
21 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 365.8032 | 3658.0319 | 10 | 365.8032 | 3658.0319
22 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 1 | 4787.15 | 4787.15 | 1 | 4787.15 | 4787.15
23 | Sheet Metal deep drawn HT Meter Box | 7132404529 | Each | 1 | 4765.89 | 4765.89 | 1 | 4765.89 | 4765.89
24 | Test terminal Box (TTB) | 7131397678 | Each | 1 | 2223.5 | 2223.5 | 1 | 2223.5 | 2223.5
25 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 74527.91 |  |  | 118272.6636
26 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 63159.2457 |  |  | 100231.0709
27 | Incidental Charges @ 7.5% on Serial no. 26 : - |  |  |  | 0.075 | 4736.9434 |  | 0.075 | 7517.3303
28 | Labour charges for concreting |  | Cmt | 2.3 | 740.31 | 1702.713 | 2.5 | 740.31 | 1850.775
29 | Back filling of PCC Pole with boulders @ 0.35 Cmt per pole |  | No | 0 | 472.92 | 0
30 | Labour charges as per Schedule No.- AL-8 |  |  |  |  | 21611.98 |  |  | 22929.82
31 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 26 |  |  |  | 0.02 | 1263.1849 |  | 0.02 | 2004.6214
32 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 26, 27, 28,29, 30, 31(i) |  |  |  |  | 11559.2584 |  |  | 16816.7022
33 | Total Estimated Cost excluding GST (Serial No 26, 27, 28,29, 30, 31(i), 32) |  |  |  |  | 104033.3255 |  |  | 151350.3198
34 | Applicable CGST @ 9% on Serial No 33 |  |  |  | 0.09 | 9362.9993 |  | 0.09 | 13621.5288
35 | Applicable SGST @ 9% on Serial No 33 |  |  |  | 0.09 | 9362.9993 |  | 0.09 | 13621.5288
36 | Total Estimated Cost including GST (Serial No 33+34+35) |  |  |  |  | 122759.3241 |  |  | 178593.3774
37 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 122759 |  |  | 178593
Note:-
1 | This Schedule is to be supplemented with Schedule A-1 & A-3.
2 | All the rates are with considering price variation clause.
3 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.

## A-9
COST SCHEDULE A-9
SCHEDULE FOR LAST SPAN CABLING OF 33 kV LINE USING COVERED CONDUCTOR OF 70 & 99 SQ.MM SIZE
2026-27
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | Qty | Using 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) long H-Beam
[6 empty] | 70 sq.mm Covered Conductor | 99 sq.mm Covered Conductor
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | H-Beam 152x152 mm 37.1 Kg/Mtr 13 M (482.30 Kg) x 1 No = 482.3 Kgs | 7130601958 | Kg | 53.0776 | 482.3 | 25599.3168 | 25599.3168
2 | 33 kV Covered conductor 70 sq.mm (207 Amp) (with 3% sag) | 7130310045 | Mtr. | 532.63 | 150 | 79894.5
3 | 33 kV Covered conductor 99 sq.mm (258 Amp) (with 3% sag) | 7130310046 | Mtr. | 582.21 | 150 |  | 87331.5
4 | 33 kV Polymer Disc Insulator | 7130820013 | Each | 187.29 | 6 | 1123.74 | 1123.74
5 | Tension / anchoring Clamp with tracking protection IPC | 7130320050 | No. | 1218.98 | 6 | 7313.88 | 7313.88
6 | Mechanical conductor with heat shrunk sleeve for bare to covered | 7130320052 | No | 1194.48 | 6 | 7166.88 | 7166.88
7 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | No | 378.54 | 3 | 1135.62 | 1135.62
8 | Earthing Coil 8 SWG GI Wire 50 mm dia 450 m | 7130870013 | No. | 143.69 | 1 | 143.69 | 143.69
9 | Single Pole Cut Point Fitting 100x50 mm | 7130810681 | Set | 3548.55 | 2 | 7097.1 | 7097.1
10 | Stay Set 20 mm | 7130860033 | No | 1080.47 | 2 | 2160.94 | 2160.94
11 | Stay Wire 7/8 SWG @ 8.5 Kg/Pole | 7130860076 | Kg | 87.2738 | 17 | 1483.6549 | 1483.6549
12 | Concreting of pole @ 0.6 Cmt per pole; @ 0.05 Cmt per pole for base padding & @ 0.3 Cmt per Stay (1:3:6) | 7130200202 | Cmt | 2970 | 1.25 | 3712.5 | 3712.5 | Rate are inclusive of all T&P and labour charges and GST
13 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 1 | 183.37 | 183.37
14 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 1 | 409.72 | 409.72
15 | Barbed Wire (@ 2 Kg/Pole) | 7130610206 | Kg | 84.3145 | 2 | 168.6291 | 168.6291
16 | Danger Board | 7130880041 | No | 101.61 | 1 | 101.61 | 101.61
17 | Stay Clamp for "H" Beam | 7130810692 | Pair | 362.75 | 4 | 1451 | 1451
18 | M.S. Nuts & Bolts 16x40 mm | 7130620609 | Kg | 86.95 | 5 | 434.75 | 434.75
19 | M.S. Nuts & Bolts 16x65 mm | 7130620614 | Kg | 85.5 | 1 | 85.5 | 85.5
20 | Dead end Assembly (Suitable for all size cable) | 7130320044 | No. | 1163.86 | 0 | 0 | 0
21 | GI earthing pipe of 40 mm dia 3.04 mtr long, 4 mm thickness 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 870.41 | 3 | 2611.23 | 2611.23
22 | Cable tie for AB Cable | 7130320045 | No | 34.57 | 0 | 0 | 0
23 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 142277.6309 | 149714.6309
24 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 120574.2635 | 126876.8058
25 | Incidental Charges @ 7.5% on Serial no. 24 : - |  |  | 0.075 |  | 9043.0698 | 9515.7604
26 | Labour Charges as per labour schedule AL-9 |  |  | 13038.47 | 1 | 13038.47 | 13038.47
27 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 24 |  |  |  | 0.02 | 2411.4853 | 2537.5361
28 | Labour charges for concreting |  | Cmt | 740.31 | 1.25 | 925.3875 | 925.3875
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 3361.28 | 2 | 6722.56 | 6722.56
30 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 24, 25, 26, 27 (i), 28, 29 |  |  |  |  | 19089.4045 | 19952.065
31 | Total Estimated Cost excluding GST (Serial No 24, 25, 26, 27(i), 28, 29, 30) |  |  |  |  | 171804.6405 | 179568.5849
32 | Applicable CGST @ 9% on Serial No 31 |  |  | 0.09 |  | 15462.4176 | 16161.1726
33 | Applicable SGST @ 9% on Serial No 31 |  |  | 0.09 |  | 15462.4176 | 16161.1726
34 | Total Estimated Cost including GST (Serial No 31+32+33) |  |  |  |  | 202729.4758 | 211890.9301
35 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 202729 | 211891
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.
3 | Use of Covered conductor, which was earlier restricted to only in last span of HT consumers remains the same; but if necessary it should be provided in line after prior approval from ED(O&M) Raipur.

## A-10
COST SCHEDULE A-10
SCHEDULE FOR 33 kV UNDERGROUND CABLE CROSSING UNDER RAILWAY TRACK / ROAD FOR 60 MTR. LONG CORRIDOR / ROUTE LENGTH OF G.I. PIPE/HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE USING OPEN TRENCH METHOD.
2026-27
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | For Railway works |  | For Road crossing works
[6 empty] | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 7 | 8
1 | G.l. Pipe 150 mm OD (Class B as per railway) | 7130641035 | Mtr | 1487.06 | 120 | 178447.2 | 178447.2
2 | HDPE pipe of size 160 mm OD/140 mm ID PN 10 PE 100 HDR | 7132461804 | Mtr | 1294.34 | 120 |  |  | 155320.8 | 155320.8
3 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 560.41 | 20 |  |  | 11208.2 | 11208.2
4 | 33 kV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 2930.9191 | 180 | 527565.4416 |  | 527565.4416
5 | 33 kV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 3202.9493 | 190 |  | 608560.3613 |  | 608560.3613
6 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 30922.07 | 4 | 123688.28 |  | 123688.28
7 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 45866.77 | 4 |  | 183467.08 |  | 183467.08
8 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 1106.27 | 24 | 26550.48 | 26550.48 | 26550.48 | 26550.48
9 | Back Clamp Rail for H-Beam | 7130810361 | Pair | 347.95 | 5 | 1739.75 | 1739.75 | 1739.75 | 1739.75
10 | M.S.Channel 100x50 mm | 7130600230 | kg | 45.5205 | 30 | 1365.6138 | 1365.6138 | 1365.6138 | 1365.6138
11 | Caping of G.I. Pipe/HDPE Pipe on both ends using end caps and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000 | 6000 | 6000
12 | M.S.Flat (50x6) mm | 7130600173 | kg | 51.0754 | 100 | 5107.541 | 5107.541 | 5107.541 | 5107.541
13 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 4 | 2224 | 2224 | 2224 | 2224
14 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 34.5 | 80 | 2760 | 2760 | 2760 | 2760
15 | Sand | 7132498006 | Cmt | 737.1 | 1.2 | 884.52 | 884.52 | 884.52 | 884.52
16 | concreting for repairing of road | 7130200001 | Cmt | 3552 | 9.6 | 34099.2 | 34099.2 | 34099.2 | 34099.2
17 | 33 kV Porcelain Lightning Arrestors | 7130840021 | Each | 4289.09 | 6 | 25734.54 | 25734.54 | 25734.54 | 25734.54
18 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 89.5109 | 18 | 1611.1969 | 1611.1969 | 1611.1969 | 1611.1969
19 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 380.53 | 6 | 2283.18 | 2283.18 | 2283.18 | 2283.18
20 | T-clamp for lightning arrestor | 7130830586 | No. | 304.09 | 6 | 1824.54 | 1824.54 | 1824.54 | 1824.54
21 | Bi-metallic clamp for earthing | 7130830603 | No. | 459.86 | 4 | 1839.44 | 1839.44 | 1839.44 | 1839.44
22 | Bhatta bricks for manufacturing of 2 Nos. chambers at both end | 7132498054 | No. | 6.57 | 128 | 840.96 | 840.96 | 840.96 | 840.96
23 | Cement | 7130200401 | Bags | 354 | 2 | 708 | 708 | 708 | 708
24 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 870.41 | 10 | 8704.1 | 8704.1 | 8704.1 | 8704.1
25 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway / Road constructing authorities including liaisoning work etc. |  | LS | LS | LS | 25000 | 25000
26 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 978977.9833 | 1119751.703 | 942059.7833 | 1082833.503
27 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 829642.3587 | 948942.1212 | 798355.7486 | 917655.511
28 | Incidental Charges @ 7.5% on Serial no. 27 : - |  |  | 0.075 |  | 62223.1769 | 71170.6591 | 59876.6811 | 68824.1633
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 3361.28 | 10 | 33612.8 | 33612.8 | 33612.8 | 33612.8
30 | Service in lieu on concreting |  | Cmt | 740.31 | 9.6 | 7106.976 | 7106.976 | 7106.976 | 7106.976
31 | Labour Charges as per Schedule - AL-6 |  | Mtr |  |  | 267308.13 | 291131.43 | 175475.7297 | 199299.0307
32 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 27 |  |  |  | 0.02 | 16592.8472 | 18978.8424 | 15967.115 | 18353.1102
33 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 27,28,29,30,31,32(i) |  |  |  |  | 152060.7861 | 171367.8536 | 136299.3813 | 155606.4489
34 | Total Estimated Cost excluding GST (Serial No 27,28,29,30,31,32(i),33) |  |  |  |  | 1368547.0749 | 1542310.6823 | 1226694.4317 | 1400458.0402
35 | Applicable CGST @ 9% on Serial No 34 |  |  | 0.09 |  | 123169.2367 | 138807.9614 | 110402.4989 | 126041.2236
36 | Applicable SGST @ 9% on Serial No 34 |  |  | 0.09 |  | 123169.2367 | 138807.9614 | 110402.4989 | 126041.2236
37 | charges payable to Railway including supervision charges etc |  |  | 15% |  | 205282.0612 | 231346.6023 | 184004.1648 | 210068.706
38 | Total Estimated Cost including GST (Serial No 34+35+36+37) |  |  |  |  | 1820167.6097 | 2051273.2075 | 1631503.5941 | 1862609.1935
39 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1820168 | 2051273 | 1631504 | 1862609
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
The rates mentioned at S.No.1, 2, 3 ,4 & 5 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
** | The charges to be paid for according railway permisssion shall be made as per actuals i.e. based on the demand note / payment received for the same.
Note:-
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | All the rates are with considering price variation clause.
3 | The Estimate should be prepared including spare cable when proposed feeder laying radial
*
**
**

## A-11
COST SCHEDULE A-11
SCHEDULE FOR LAYING OF 1 kM 33 kV CABLE DIRECT IN GROUND SINGLE CABLE LINE USING OPEN TRENCH METHOD
2026-27
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | 3x240 sq.mm AB XLPE Cable | 3x400 sq.mm AB XLPE Cable
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | 33 KV XLPE 240 sqmm 3 core UG Cable | 7130310075 | Mtr | 2930.9191 | 1040 | 3048155.8848
2 | 33 KV XLPE 400 sqmm 3 core UG Cable | 7130310020 | Mtr | 3202.9493 | 1040 |  | 3331067.2408
3 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 120- 240 sq mm Underground XLPE cable | 7130310089 | Set | 76738.73 | 2 | 153477.46
4 | Straight through heat shrinkable cable jointing kit with lugs for 3 core 300- 400 sq mm Underground XLPE cable | 7130310090 | No | 85933.91 | 2 |  | 171867.82
5 | End terminating jointing kit upto 240 sqmm XLPE cable | 7130352037 | Set | 30922.07 | 2 | 61844.14
6 | End terminating jointing kit for 400 sqmm XLPE cable | 7130352010 | Set | 45866.77 | 2 |  | 91733.54
7 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | 7130640027 | RM | 1106.27 | 10 | 11062.7 | 11062.7
8 | G.I. Wire 8 SWG (for earthing connect to LA & cable) | 7130870043 | Kg | 69.8234 | 5 | 349.1168 | 349.1168
9 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No | 556 | 20 | 11120 | 11120
10 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 34.5 | 4000 | 138000 | 138000
11 | River Sand (For 10 cm. base & 10 cm. filling of trench above cable & then cable covering tiles over complete length of trench) | 7132498006 | Cmt | 737.1 | 150 | 110565 | 110565
12 | 33 KV Polymer Lightning Arrestors | 7130840021 | Each | 4289.09 | 6 | 25734.54 | 25734.54
13 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 89.5109 | 18 | 1611.1969 | 1611.1969
14 | Aluminium T-clamp suitable for Dog / Raccoon conductor for connecting L.A. | 7130830585 | No. | 380.53 | 6 | 2283.18 | 2283.18
15 | Bi-metallic clamp for earthing | 7130830603 | No. | 459.86 | 4 | 1839.44 | 1839.44
16 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. | 7130642039 | No | 870.41 | 10 | 8704.1 | 8704.1
17 | M.S. Nuts & Bolts | Fill the appropriate Bin Code | Kg |  | 3 | 0 | 0
18 | Bhatta brick | 7132498054 | No | 6.57 | 4400 | 28908 | 28908
19 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from Road constructing authorities including liaisoning work etc. [ To be provisioned as per actual requirement ] |  | LS | LS | LS | 25000 | 25000
20 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 3628654.7585 | 3959845.8745
21 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 3075131.1512 | 3355801.5885
22 | Incidental Charges @ 7.5% on Serial no. 21 : - |  |  | 0.075 |  | 230634.8363 | 251685.1191
23 | Service in lieu of Earthing Coal & Sand etc |  | No | 3361.28 | 10 | 33612.8 | 33612.8
24 | Labour Charges as per Schedule AL-11 |  |  |  |  | 968065.04 | 1073245.48
25 | Supervision charges @ 15% Serial no. 21, 23, 24 |  |  | 0.15 |  | 611521.3487 | 669398.9803
26 | Transportation charges of all line materials :-
(i) | Upto 100 km @ 2% on Serial no. 21 |  |  | 0.02 |  | 61502.623 | 67116.0318
27 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. - 21, 22, 23, 24, 26(i) |  |  |  |  | 546118.3063 | 597682.6274
28 | Total Estimated Cost excluding GST (Serial No 21, 22, 23, 24, 25, 26(i), 27) |  |  |  |  | 5526586.1056 | 5990664.9956
29 | Applicable CGST @ 9% on Serial No 28 |  |  | 0.09 |  | 497392.7495 | 539159.8496
30 | Applicable SGST @ 9% on Serial No 28 |  |  | 0.09 |  | 497392.7495 | 539159.8496
31 | Charges payable to Nagar Nigam / Nagar Palika / Nagar Panchayat / Gram Panchayat as per Demand note. |  | LS |  |  | 200000 | 200000
32 | Total Estimated Cost including GST (Serial No 28+29+30+31) |  |  |  |  | 6721371.6046 | 7268984.6948
33 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 6721372 | 7268985
Note:-
(a) | Cable and accessories size can be replaced as per actual requirement
(b) | When multiple cables have to be laid in the common trench, the following excavation is to be followed-- (i) 1.0 Mtr width x 1.5 Mtr depth for laying of 02 cables; (ii) 1.25 Mtr width x 1.5 Mtr depth for laying of 03 cables; (iii) 1.5 Mtr width x 1.5 Mtr depth for laying of 04 cables and so on.
(c) | Between two cables, fly ash brick is to be provided as separator
(d) | All other items are to be changed as per size of trench and number of cables in a trench.
1 | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
2 | Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
3 | All the rates are with considering price variation clause.
4 | The Estimate should be prepared including spare cable when proposed feeder laying radial
Fill appropriate cost
Fill appropriate cost
Fill appropriate cost200000.00
Fill appropriate cost
Note on G41: Author: Fill appropriate cost (LS amt. 200000.00 taken for calculation)
Note on H41: Author: Fill appropriate cost (LS amt. 200000.00 taken for calculation)

## A-12(A)
COST SCHEDULE A-12(A)
2026-27
COST PER KM OF 33 kV OVERHEAD AB CABLE LINE SUITABLE TO 95 / 150 Sqmm. ON H - BEAM POLE WITH AVERAGE SPAN 25 MTRS.
Assumed as if cable length is 250 Mtr. in one stroke.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Using 33 kV 3 core A.B. XLPE Cable of size 95 sqmm |  | Using 33 kV 3 core A.B. XLPE Cable of size 150 sqmm
[5 empty] | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 40 Nos = 16324 Kgs | 7130601965 | Kg | 52.6646 | 16324 | 859696.6039 | 16324 | 859696.6039
2 | 33 kV XLPE 3 Core Cable 95 sqmm (incl. sag 6%) | 7130310051 | Mtr. | 1371.5123 | 1060 | 1453803.0804
3 | 33 kV XLPE 3 Core Cable 150 sqmm (incl. sag 6%) | 7130310052 | Mtr. | 1683.6096 |  |  | 1060 | 1784626.2184
4 | 33 kV End Termination kit for XLPE Cable 95-120 sqmm | 7130320038 | Set | 17112.3 | 2 | 34224.6
5 | 33 kV End Termination kit for XLPE Cable 185 sqmm | 7130320039 | Set | 20534.75 |  |  | 2 | 41069.5
6 | 33 kV Straight thru' joint kit suitable upto 120 sqmm Cable post Insulator mounted busbar through joint,one post insulator for each phase | 7130310056 | Set | 34224.59 | 3 | 102673.77
7 | 33 kV AB Cable Straight thru' joint kit suitable for 185 sqmm | 7130310088 | Set | 45506.95 |  |  | 3 | 136520.85
8 | Earth spike | 7130870010 | No. | 997.81 | 6 | 5986.86 | 6 | 5986.86
9 | 33 KV Cut Point Channel | 7130810681 | Set | 3548.55 | 0 | 0 | 0 | 0
10 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 3137.26 | 8 | 25098.08 | 8 | 25098.08
11 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 2788.67 | 36 | 100392.12 | 36 | 100392.12
12 | Cable Tie | 7130820029 | No. | 43.21 | 200 | 8642 | 200 | 8642
13 | Strain Plate | 7130810624 | set | 101.05 | 0 | 0 | 0 | 0
14 | Stay set without stay wire 20 mm | 7130860033 | No. | 1080.47 | 12 | 12965.64 | 12 | 12965.64
15 | Stay wire 7/8 SWG 10 kg/stay | 7130860076 | Kg | 87.2738 | 120 | 10472.8584 | 120 | 10472.8584
16 | Stay clamp for H-Beam | 7130810692 | No. | 362.75 | 24 | 8706 | 24 | 8706
17 | Clamp for H-Beam 2.5 pair*40 | 7130810692 | No. | 362.75 | 0 | 0 | 0 | 0
18 | M.S.Angle 65x65x6 mm 5.8*1*40 | 7130600032 | Kg | 45.5205 | 0 | 0 | 0 | 0
19 | G.I. Wire 4.0 mm (8 SWG) [ @ 1 kg /pole ] | 7130870043 | Kg | 69.8234 | 40 | 2792.934 | 40 | 2792.934
20 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 40 | 7334.8 | 40 | 7334.8
21 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 40 | 16388.8 | 40 | 16388.8
22 | Earthing Coil | 7130870013 | No. | 143.69 | 40 | 5747.6 | 40 | 5747.6
23 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 84.3145 | 80 | 6745.164 | 80 | 6745.164
24 | Danger Board | 7130880041 | No. | 101.61 | 40 | 4064.4 | 40 | 4064.4
25 | Concreting of supports @ 0.6 Cmt. Per pole for H-Beam ; and @ 0.3 Cmt per stay and @ 0.05 Cmt per pole for base padding for PCC / H-Beam pole. (1:3:6) | 7130200202 | Cmt | 2970 | 29.6 | 87912 | 29.6 | 87912
26 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4289.09 | 6 | 25734.54 | 6 | 25734.54
27 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 89.5109 | 18 | 1611.1969 | 18 | 1611.1969
28 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 380.53 | 6 | 2283.18 | 6 | 2283.18
29 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 870.41 | 10 | 8704.1 | 10 | 8704.1
30 | M.S.Nuts and Bolts |  | Kg |  | 55 |  | 55
| 16x65 mm | 7130620614 | Kg | 85.5 | 35 | 2992.5 | 35 | 2992.5
| 16x200 mm | 7130620631 | Kg | 84.05 | 20 | 1681 | 20 | 1681
31 | SUB TOTAL-1 |  |  |  |  | 2796653.8276 |  | 3168168.9456
32 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 2370045.6166 |  | 2684888.937
33 | Incidental Charges @ 7.5% on serial no 32 |  |  | 0.075 |  | 177753.4212 |  | 237612.6709
34 | Labour charges as per Schedule No.- AL-12 |  |  |  |  | 208041.77 |  | 250250.97
35 | Service in lieu of Concreting |  | Cmt | 740.31 | 29.6 | 21913.176 | 29.6 | 21913.176
36 | Service in lieu of Earthing Coal & Salt etc |  | No. | 3361.28 | 10 | 33612.8 | 10 | 33612.8
37 | Transportation charges of all line materials
(i) | upto 100 km @ 2% on Serial no. 32 |  |  | 0.02 |  | 47400.9123 |  | 53697.7787
38 | Overhead Charges @ 12.5% [Market Fluctuation, Contractor's profit etc.] on Serial no. - 32,33,34,35,36,37(i) |  |  |  |  | 357345.962 |  | 410247.0416
39 | Total Estimated Cost excluding GST (Serial No 32,33,34,35,36,37(i),38 |  |  |  |  | 3216113.6583 |  | 3692223.3742
40 | Applicable CGST @ 9% on Serial No 39 |  |  | 0.09 |  | 289450.2292 |  | 332300.1037
41 | Applicable SGST @ 9% on Serial No 39 |  |  | 0.09 |  | 289450.2292 |  | 332300.1037
42 | Total Estimated Cost including GST (Serial No 39+40+41) |  |  |  |  | 3795014.1167 |  | 4356823.5816
43 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 3795014 |  | 4356824
Note:-
(1)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
(2)Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
(3) All the rates are with considering price variation clause.
*
*

## A-12(B)
COST SCHEDULE A-12(B)
2026-27
COST PER KM OF 33 kV OVERHEAD AB CABLE LINE ON H - BEAM POLE WITH AVERAGE SPAN 20 MTRS SUITABLE ABOVE 150 Sqmm.
Assumed as if cable length is 250 Mtr. in one stroke.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Using 33 kV 3 core A.B. XLPE Cable of size 185 sqmm |  | Using 33 kV 3 core A.B. XLPE Cable of size 240 sqmm
[5 empty] | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 50 Nos = 20405 Kgs | 7130601965 | Kg | 52.6646 | 20405 | 1074620.7549 | 20405 | 1074620.7549
2 | 33 kV XLPE 3 Core Cable 185 sqmm (incl. sag 6%) | 7130310053 | Mtr. | 1924.2985 | 1060 | 2039756.4312
3 | 33 kV XLPE 3 Core Cable 240 sqmm (incl. sag 6%) | 7130310054 | Mtr. | 2446.9444 |  |  | 1060 | 2593761.0746
4 | 33 kV AB Cable Straight thru' joint kit suitable for 185 sqmm | 7130310088 | Set | 45506.95 | 3 | 136520.85
5 | 33 kV Straight thru' joint kit suitable for 240 sqmm Cable post Insulator mounted busbar through joint,one post insulator for each phase | 7130352037 | Set | 30922.07 |  |  | 3 | 92766.21
6 | 33 kV ABC Termination kit for XLPE Cable 185 sqmm | 7130320039 | Set | 20534.75 | 2 | 41069.5
7 | 33 kV ABC Termination kit for XLPE Cable 240 sqmm | 7130320040 | Set | 23957.22 |  |  | 2 | 47914.44
8 | Earth spike | 7130870010 | No. | 997.81 | 6 | 5986.86 | 6 | 5986.86
9 | 33 KV Cut Point Channel | 7130810681 | Set | 3548.55 | 0 | 0 | 0 | 0
10 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 3137.26 | 8 | 25098.08 | 8 | 25098.08
11 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 2788.67 | 46 | 128278.82 | 46 | 128278.82
12 | Cable Tie | 7130820029 | No. | 43.21 | 200 | 8642 | 200 | 8642
13 | Strain Plate | 7130810624 | set | 101.05 | 0 | 0 | 0 | 0
14 | Stay set without stay wire 20 mm | 7130860033 | No. | 1080.47 | 12 | 12965.64 | 12 | 12965.64
15 | Stay wire 7/8 SWG 10 kg/stay | 7130860076 | Kg | 87.2738 | 120 | 10472.8584 | 120 | 10472.8584
16 | Stay clamp for H-Beam | 7130810692 | No. | 362.75 | 24 | 8706 | 24 | 8706
17 | Clamp for H-Beam 2.5*50 | 7130810692 | No. | 362.75 | 0 | 0 | 0 | 0
18 | M.S.Angle 65x65x6 mm | 7130600032 | Kg | 45.5205 | 0 | 0 | 0 | 0
19 | G.I. Wire 4.0 mm (8 SWG) [ @ 1 kg /pole ] | 7130870043 | Kg | 69.8234 | 50 | 3491.1675 | 50 | 3491.1675
20 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 50 | 9168.5 | 50 | 9168.5
21 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 50 | 20486 | 50 | 20486
22 | Earthing Coil | 7130870013 | No. | 143.69 | 50 | 7184.5 | 50 | 7184.5
23 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 84.3145 | 100 | 8431.455 | 100 | 8431.455
24 | Danger Board | 7130880041 | No. | 101.61 | 50 | 5080.5 | 50 | 5080.5
25 | Concreting of Pole @ 0.65 Cmt per pole and 0.3 Cmt per stay | 7130200202 | Cmt | 2970 | 36.1 | 107217 | 36.1 | 107217
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 354 | 0 | 0 | 0 | 0
26 | 33 kV Polymer Lightning Arrestors | 7130840021 | Each | 4289.09 | 6 | 25734.54 | 6 | 25734.54
27 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 89.5109 | 18 | 1611.1969 | 18 | 1611.1969
28 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 380.53 | 6 | 2283.18 | 6 | 2283.18
29 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 870.41 | 10 | 8704.1 | 10 | 8704.1
30 | M.S.Nuts and Bolts |  | Kg |  | 65 |  | 65
| 16x65 mm | 7130620614 | Kg | 85.5 | 40 | 3420 | 40 | 3420
| 16x200 mm | 7130620631 | Kg | 84.05 | 25 | 2101.25 | 25 | 2101.25
31 | SUB TOTAL-1 |  |  |  |  | 3697031.1839 |  | 4214126.1273
32 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 3133077.2745 |  | 3571293.3282
33 | Incidental Charges @ 7.5% on serial no 32 |  |  | 0.075 |  | 234980.7956 |  | 267846.9996
34 | Labour charges as per Schedule No.- AL-12 |  |  |  |  | 285769.47 |  | 285769.47
35 | Service in lieu of Concreting |  | Cmt | 740.31 | 36.1 | 26725.191 | 36.1 | 26725.191
36 | Service in lieu of Earthing Coal & Salt etc |  | No. | 3361.28 | 10 | 33612.8 | 10 | 33612.8
37 | Transportation charges of all line materials
(i) | upto 100 km @ 2% on Serial no. 32 |  |  | 0.02 |  | 62661.5455 |  | 71425.8666
38 | Overhead Charges @ 12.5% [Market Fluctuation, Contractor's profit etc.] on Serial no. - 32,33,34,35,36,37(i) |  |  |  |  | 472103.3846 |  | 532084.2069
39 | Total Estimated Cost excluding GST (Serial No 32,33,34,35,36,37(i),38 |  |  |  |  | 4248930.4612 |  | 4788757.8623
40 | Applicable CGST @ 9% on Serial No 39 |  |  | 0.09 |  | 382403.7415 |  | 430988.2076
41 | Applicable SGST @ 9% on Serial No 39 |  |  | 0.09 |  | 382403.7415 |  | 430988.2076
42 | Total Estimated Cost including GST (Serial No 39+40+41) |  |  |  |  | 5013737.9442 |  | 5650734.2776
43 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 5013738 |  | 5650734
Note:-
(1)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
(2)Schedule A-2 (B) is to be supplemented with every 1.0 Km of 33 kV line.
(3) All the rates are with considering price variation clause.
*
*