## COMPARATIVE
COMPARATIVE STATEMENT OF RATES FROM YEAR 2025-26 to 2026-27
S. No. | Particulars of Schedules |  | Schedule Reference | Unit | 2025-26 | 2026-27 | %tage Incr. / Decr. in cost
[5 empty] | TOTAL COST | TOTAL COST
1 | 2 |  | 3 | 4 | 5 | 6 | 7
Part-II, 33/11 kV SUB-STATIONS
(A) |  | New Sub-stations:
| i | 1.6 MVA, 33/11 kV S/s expandable to 2 x 1.6 MVA with control room | B-1(i) | Each | 12548087 | 13198484 | 5.1832
| ii | 3.15 MVA, 33/11 kV S/s expandable to 2 x 3.15 MVA with control room | B-1(ii) | Each | 15872440 | 16888002 | 6.3983
| iii | 5 MVA, 33/11 kV S/s expandable to 2 x 5 MVA with control room | B-1(iii) | Each | 19062450 | 20259349 | 6.2788
(B) |  | 33/11 kV Power Transformer
| i | 1.6 MVA | B-2(i) | Each | 1736592 | 1921315 | 10.6371
| ii | 3.15 MVA | B-2(ii) | Each | 4999806 | 5548633 | 10.977
| iii | 5.0 MVA | B-2(iii) | Each | 6933436 | 7543917 | 8.8049
(C) |  | Installation of additional transformer for parallel operation with one additional bay on 11 kV side
| i | 1.6 MVA | B-3(i) | Each | 5122391 | 5410333 | 5.6212
| ii | 3.15 MVA | B-3(ii) | Each | 8809363 | 9517258 | 8.0357
| iii | 5.0 MVA | B-3(iii) | Each | 10742993 | 11512541 | 7.1633
(D) |  | 11 kV Out door yard extension for additional bay with circuit breaker. | B-4 | Each | 815555 | 840055 | 3.0041
(E) |  | 33 kV Out door yard extension for additional bay without circuit breaker. | B-5 | Each | 451640 | 440483 | -2.4703
(F) |  | Installation of 33 kV VCB | B-6 | Each | 545545 | 608521 | 11.5437
(G) |  | Augmentation of Power Transformer
| i | 1.6 to 3.15 MVA | B-8(i) | Each | 4901310 | 5512573 | 12.4714
| ii | 3.15 to 5.0 MVA without 33 kV VCB | B-8(ii) | Each | 5282893 | 5893923 | 11.5662
| iii | 3.15 to 5.0 MVA with 33 kV VCB | B-8(iii) | Each | 5843566 | 6516483 | 11.5155
(H) |  | Installation of 1.6 MVA 33/11 kV Sub-Station ON LINE | B-9 | Each | 2333036 | 2509005 | 7.5425
(I) | (i) | SCHEDULE FOR 33/11 SUB-STATION CHEMICAL EARTHING (Soil excavation through Manual machine) | B-10(i) | Each | 358170 | 393638 | 9.9026
| (ii) | SCHEDULE FOR 33/11 SUB-STATION CHEMICAL EARTHING (Soil excavation through Boring Machine) | B-10(ii) | Each | 362758 | 398225 | 9.777

## SOR RATE 2026-27
RATE OF STOCK MATERIALS IN SoR OF 2026-27
RATE OF ALL MATERIALS ARE INCLUSIVE OF G.S.T. UNLESS MENTIONED SPECIFICALLY IN REMARKS COLUMN
Material Code | Description | Unit | Unit rate for 2026-27 | SAP DESCRIPTION | REMARKS
7130200201 | 1:1.5:3 Ratio | Cmt | 4073 |  |  | Rate are inclusive of all T&P and labour charges
7130200001 | 1:2:4 Ratio | Cmt | 3552 |  |  | Rate are inclusive of all T&P and labour charges
7130200202 | 1:3:6 Ratio | Cmt | 2970 |  |  | Rate are inclusive of all T&P and labour charges
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 207.78 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 354 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Each | 34.5 |  |  | Rate are inclusive of all T&P and labour charges
7130210809 | Aluminium Paint | Ltr. | 409.72 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 313.68
7130211158 | Red Oxide Paint | Ltr. | 183.37 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 345952.9 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5 | ISI MARK
7130310007 | 70 Sqmm. | Km. | 84041.77 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V | ISI MARK
7130310008 | 120 Sqmm. | Km. | 153470.73 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100 | ISI MARK
7130310020 | 33 kV 3 CORE XLPE UG CABLE 3x400 Sq.mm. | km | 3202949.27 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 48196.36 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V | ISI MARK
7130310022 | 50 Sqmm. | Km. | 61736.86 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V | ISI MARK
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 117441.13 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM | ISI MARK
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 151505.38 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM | ISI MARK
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 181440.54 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM | ISI MARK
7130310038 | 2.5 Sqmm. | Per Mtr. | 10.26 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 43.31 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 89.74 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 174398.3 | 11KV PVC INSULATED 150SQMM SINGLE CORE X | ISI MARK
7130310042 | 16.0 Sqmm. | km | 58588.78 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 85098.78 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310005 | 25 Sq.mm. | km | 135241.73 | 11KV PVC INSULATED 25SQMM 4 CORE ARMOURE
7130310049 | 120 Sq.mm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310050 | 400 Sqmm. | km |  |  |  | ITEM DELETED: NOT TO BE USED
7130310051 | 3x95 Sq.mm. | km | 1371512.34 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1683609.64
7130310053 | 3x185 Sq.mm. | km | 1924298.52 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 2446944.41 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 23957.22
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 34224.59
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 538738.83 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 763567.97
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 926693.2
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 1082726.04
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 5228.76 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 5502.44 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 80025.06 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 237497.47 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM | ISI MARK
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 237497.47 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310068 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x95+1x16+1x70 | km | 441600.55
7130310092 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3x120+1x16+1x95 | km | 551312.67
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 85297.43 | LT AB CABLEB 3X16+1X25 SQMM | ISI MARK
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 86469.51 | LT AB CABLEB 3X25+1X25 SQMM | ISI MARK
7130640032 | 33 kV 3 CORE XLPE UG CABLE 3X 150 SQMM | km | 1943588.25 | 33 kV 3 CORE XLPE UG CABLE 3X 150 SQMM
7130310075 | 33 kV 3 CORE XLPE UG CABLE 3x240 Sq.mm. | km | 2930919.12 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 782172.46 | 11KV 3 CORE XLPE UG CABLE 70 SQMM
7130310077 | 95 Sq.mm | km | 791365.28 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 1180085.11 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 1429802.53 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 2202958.24 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310082 | PVC Insulated 1100 Volts grade Aluminium Twin Core Single Phase 4.0 sq.mm. Unarmoured service cable. | Per Mtr. | 20.16 | PVC Insulated 11kV 2 Core 4.0 sqmm cable
7130310083 | PVC Insulated 1100 Volts grade 70 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 501251.82 | PVC Insul. 70 Sqmm 4C Armour UG AL. Cable
7130310084 | PVC Insulated 1100 Volts grade 95 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 611203.83 | PVC Insul. 95 Sqmm 4C Armour UG AL Cable
7130310085 | PVC Insulated 1100 Volts grade 150 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 922734.53 | PVC Insu. 150 Sqmm 4C Armour UG Al Cable
7130310086 | PVC Insulated 1100 Volts grade 300 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 1762466.07 | PVC Insul. 300 Sqmm. 4C Armour Al. Cable
7130310087 | PVC Insulated 1100 Volts grade 400 SQMM, 4 CORE, ARMOURED AL. CABLE | km | 2240002.75 | PVC Insul. 400 Sqmm. 4C Armour Al. Cable
7130310088 | 33 kV AB Cable Straight thru' joint kit suitable for 185 sqmm | Set | 45506.95 | 33 kV ABC Straight thru jointkit 185 sqmm
7130310089 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 120-240 sq mm XLPE cable | Set | 76738.73 | 33kV UGCable Straight thru jointkit 120-240 sqmm
7130310090 | 33 kV XLPE UG Cable Straight through heat shrinkable cable jointing kit with lugs for 3 core 300-400 sq mm XLPE cable | No | 85933.91 | 33kV UGCable Straight thru jointkit 300-400 sqmm
7130310652 | 2 Core (UNARMOURED) | Km. | 72362.33 | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 2 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310654 | 4 Core (UNARMOURED) | Km. | 132305.02 | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. |  | CONTROL CABLE COP 4 CORE 2.5 SQMM PVC/PVC |  | ITEM DELETED: NOT TO BE USED
7130310658 | 8 Core (UNARMOURED) | Km. | 253252.8 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310681 | 10 Core (UNARMOURED) | Km. | 319624.96 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 365803.19 | CONTROL CABLE COP 10 CORE 2.5 SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 329371.81 | CONTROL CABLE COP 12 CORE 2.5 SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 29483.67 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 70493.34 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 95818.1 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 189275.23 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 374426.47 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 469301.42 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC |  | ITEM DELETED: NOT TO BE USED
7130311057 | 150 Sqmm. | km |  | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV |  | ITEM DELETED: NOT TO BE USED
7130311061 | 300 Sqmm. | km |  | Power Cable ARM ALU 3.5CORE 300/150SQMM |  | ITEM DELETED: NOT TO BE USED
7130311084 | 16.0 Sqmm. | km | 89546.69 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 13689.84
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 17112.3 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 20534.75 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 23957.22 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 25668.45
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 30802.14
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 1077.45 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 1163.86
7130320045 | Cable tie for AB Cable | Each | 34.57
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | No | 5192.06 | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 3311.54 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 3488.72
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 7.24 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 45866.77 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 1110.58 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352031 | 16 Sq.mm, 4 Core | Set | 1110.58 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 1192.67
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1676.66
7130352034 | 150 Sq.mm, 3.5 Core | Set | 2499.15
7130352035 | 300 Sq.mm, 3.5 Core | Set | 4038.97
7130352036 | 400 Sq.mm, 3.5 Core | Set | 5161.06
7130352037 | End terminating jointing kit upto 240 sqmm XLPE cable | Set | 30922.07 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x50 Sq.mm | Set | 18483.6 | 3X50 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352039 | 3x95 Sq.mm | Set | 18483.6 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 24472.89 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 26765.34 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 26765.34 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 9608.12 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 11598.63 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 11932.29 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box (with 10 No. connectors) | No. | 4080.55 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 3.09 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 3.09 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 6.18
7130354277 | 32 Sq mm | Nos. | 7.73
7130354278 | 50 Sq mm | Nos. | 12.39 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 18.57 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 23.21 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 32.51 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 37.14 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 58.81
7130354284 | 225 Sq mm | Nos. | 66.54
7130354285 | 240 Sq mm | Nos. | 95.95
7130354286 | 300 Sq mm | Nos. | 112.98 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 145.48
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 888.45 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 98.54 | INSULATING PIERCING CONNECTOR AB CABLE
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 128.38 | INSULATING PIERCING CONNECTOR FOR AB CABLE
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 178.94 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 161 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 227.52 | STRAIGHT THROUGH JOINT
7130390019 | End cap for 50/70 Sq.mm | Nos. | 38.88 | END CLAMP CAP FOR 50/70 SQMM
7130640040 | M.S. ANGLE 35 x 35 x 5 mm | MT | 38600.4 | M.S. ANGLE 35 x 35 x 5 mm
7130600023 | 50 x 50 x 6 mm | MT | 45520.46 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 45520.46 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 45520.46 | M S ANGLE 75X75X6 MM
7130600166 | 75x40 mm | MT | 45520.46 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 51075.41 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 45520.46 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 51075.41 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT |  | R.S.JOIST 125 x 70 mm |  | ITEM DELETED: NOT TO BE USED
7130600675 | 175 x 85 mm | MT | 56727.95 | R S JOIST 175X85 MM
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 70349.02 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 70349.02 | RAIL 60 KG PER METER
7130601958 | LINE SUPPORTS "H" BEAMS 152x152 mm; 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 53077.58 | H BEAMS 152X152MM; 37.1 KG/MTR.
7130601965 | LINE SUPPORTS "H" BEAMS 152x152 mm; 37.1 Kg/Mtr.; 13 Mtr. Length 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 52664.58 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR
7130600012 | Wide Parallel Flange Beam (WPB) 13 Meter long (160x160 mm) ; 30.44 Kg/Mtr. | MT | 65688.24
7130600011 | Wide Parallel Flange Beam (WPB) 11 Meter long (160x160 mm) ; 30.44 Kg/Mtr. | MT | 65452.24
7130610206 | Barbed wire | MT | 84314.55 | G.I. WIRES: - Barbed wire.
7130810243 | Rack 50x50x6 mm Angle | No | 3872.95
7130620013 | Bolt Big size | No | 155.56 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 86.95
7130620133 | 16x40 mm | Kg | 120.28 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 120.28 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 86.95 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 88.4 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 88.4 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 86.95 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 85.5 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 85.5 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 84.05 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 84.05 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt 25x12 mm | No | 520.75 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 152.82 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 sqmm cable of dia 105 mm | RM | 1106.27 | G.I. PIPE 200MM FOR 400MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 958.52 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 4090.22 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | Caping of RCC Pipe on both end of pipe with Concreting and Bricks work | Cmt | 4090.64
7130300496 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 450 mm | RM | 1769 |  |  | Rate are inclusive of all T&P and labour charges
7130640031 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 600 mm | RM | 2459 |  |  | Rate are inclusive of all T&P and labour charges
7130640036 | RCC Pipe Type NP-3 (2.5 mtr long) on first class bedding - 900 mm | RM | 4874 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG) |  | Rate are inclusive of all T&P and labour charges
7130640037 | M.S.Pipe 200 mm dia with collars | RM (medium) | 1504.96
7130640038 | M.S.Pipe 200 mm dia with collars | RM (light) | 1175.3 | M.S. PIPE 200 MM DIA WITH COLLARS
7130640171 | G.I. Bend 40 mm | Each | 106.78
7130641396 | Gl Pipe 40 mm | Per Mtr | 220.62 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | No | 870.41 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 4423.96 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. 04-01/ST/62 R2 Date 05.06.2007 | RM | JOB REPLACED |  | Job of Bin code 7130650001 has been raplaced by two types of soil strata as Hard Soil; and Black Cotton Soil | THIS JOB NOT TO BE USED FROM YEAR 2023-24
| Const. of 2.40 M high chain link wire mesh fencing on Hard Soil or Hard Moorum (Non Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete | Mtr. | 2756 |  |  | RATE EXCLUDING G.S.T.
| Const. of 2.40 M high chain link wire mesh fencing on Black Cotton Soil (Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete | Mtr. | 3176 |  |  | RATE EXCLUDING G.S.T.
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 151.17
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 794.21 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 576.46 | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 2371.18 | PCC POLE 140 KG; 8,0 MTR LONG |  | Rate are inclusive of all T&P and labour charges
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130800033 | 280 Kg; 9.1 Mtr long | Each | 4613.69 | PCC POLE 280 KG; 9.1 MTR LONG |  | Rate are inclusive of all T&P and labour charges
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each |  | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT |  | ITEM DELETED: NOT TO BE USED
7130800672 | 350 Kg; 7.0 Mtr long | Each |  | PCC POLE 350 KG; 7,0 MTR LONG |  | ITEM DELETED: NOT TO BE USED
7130810005 | Through Bolt - 12 mm | No | 109.43 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr Channel 100 x 50 mm. | Set | 7486.37 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810208 | D.C.Cross Arm 4.8 Mtr. Channel 100x50 mm | Set | 9386.55
7130870005 | Stay clamp for 140 kG PCC Pole | Pair | 175.2 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 326.97 | Stay clamp LT/Pair
7130810060 | L.T. "U" Clamp 50x6 mm Flat | No. | 87.6 | LT U CLAMP
7130810213 | Fencing Post 4 Feet Centre 75x75x6 mm | No. | 692.78
7130810214 | Fencing Post 8 Feet Centre 75x75x6 mm | No. | 1386.65
7130810215 | Fencing Post 10 Feet Centre 75x75x6 mm | No. | 1703.35
7130810217 | 33 kV Bird Guard Stool | No. | 252.91
7130810244 | 11 kV Bird Guard Stool | No. | 221.03
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 76.37 | Strain Plate
7130810077 | Pole Clamp | No. | 583.15 | POLE CLAMP
7130810102 | Service Ring | No. | 463.41 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 326.97 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 347.95 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 347.95 | HT STAY CLAMP R S JOIST A TYPE
7130810241 | Stay Clamp for R.S.Joist "B" type | Pair | 347.95
7130810251 | Stay Clamp Rail "B" type | Pair | 347.95 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 347.95 | 33 KV TOP CLAMP SEMIFINISHED
7130810219 | Back Clamp for FRC type Cross Arm | No. | 151.76
7130810220 | Back Clamp for Rail Pole Plate 65x8 mm 1 No. | No. | 347.95
7130810212 | 33 kV Bridling Top Clamps 75x75x6 mm | No. | 421.16
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 679.57 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 809.34 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 939.1 | LT FIVE PIN CROSS ARM
7130810196 | L.T. 2 Pin Cross Arm 50x50x5 mm | No. | 466.25
7130810197 | L.T. 3 Pin Cross Arm 50x50x5 mm | No. | 569.62
7130810198 | L.T. 4 Pin Cross Arm 50x50x5 mm | No. | 674.09
7130810199 | L.T. 5 Pin Cross Arm 50x50x5 mm | No. | 777.44
7130810200 | L.T. 3 Pin Cross Arm 65x65x6 mm | No. | 712.57
7130810202 | L.T. 5 Pin Cross Arm 65x65x6 mm | No. | 997.38
7130810203 | L.T. 5 Pin Cross Arm for tangent location | No. | 1120.54
7130810239 | L.T. Side Bracket 4 Pin 50x50x6 mm | No. | 803.84
7130810240 | L.T. Side Bracket 5 Pin 50x50x6 mm | No. | 3367.11
7130810495 | 11 kV Cross Arm Cleat type | No. | 1152.42 | 11 KV V CROSS ARM
7130810209 | 11 kV Bridling Cross Arm 65x65x6 mm | No. | 1709.94
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 1826.51 | D.O. / LA Mounting channel 75x40 mm.
7130810218 | D.O.Mounting Angle 75x75x6 mm | No. | 1739.08
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2732.61 | 1.1 MTR DPDC CROSS ARM
7130810231 | 11 kV Guarding Angle 100x100x6 mm | Set | 2570.96
7130810232 | Upper & Lower Cross Arm for special structures | Set | 11676
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 4332.59 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810513 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 3147.18 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810234 | D.C.Cross arm 4' Centre for special structures | Set | 4390.87
7130810514 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 4422.77 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 5000.08 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810222 | D.C.Cross arm 8' Centre 75x40 mm Channel | Set | 3645.31
7130810223 | D.C.Cross arm 8' Centre Angle type 100x100x6 mm | Set | 5064.95
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 2564.36 | 33 KV V CROSS ARM
7130810211 | 33 kV Bridling Cross Arm 75x75x6 mm | No. | 2001.35
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 5912.78 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810221 | D.C.Cross arm 5' Centre Angle type 100x100x8 mm | Set | 8489.24
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 101.05 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 426.66 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 323.29 | 11 kV top clamp
7130810210 | 11 kV Bridling Top Clamps 65x65x6 mm | No. | 609.21
7130810204 | 11 kV Cross Arm angle type 65x65x6 mm | No. | 1146.93
7130810205 | 11 kV "V" Cross Arm Channel type 75x40 mm | No. | 1411.94
7130810206 | 11 kV Top Clamp Channel type 75x40 mm | No. | 388.17
7130810207 | 11 kV Top Clamp Cleat type | No. | 285.9
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 3548.55 | 11 kV Cut point channel paint
7130810236 | Single Pole Cut Point Fitting 75x40 mm | Set | 1818.8
7130810237 | Side Cross Arm for 11 kV 50x50x6 mm | No. | 2149.8
7130810238 | Side Cross Arm for 11 kV 75x40 mm channel | No. | 2552.26
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 9299.67 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 362.75 | Stay clamp for 'H' Beam
7130810242 | Stay Clamp L.T. Rail for H-Beam | Pair | 347.95
7130820008 | 11 kV Pin insulator with Pin | Each | 139.71 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 378.54 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 111.39 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 187.29 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 5.13 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 599.74 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 2452.66 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 43.21
7130820030 | Disc insulator | Each | 314.39 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 60.51 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 310.47 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 14.36 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 16.99 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 13.68 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 95.84 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 318.93 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 50.75 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 47.98 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 54.62 | HARDWARE FOR 75X90 MM LT SHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 160.75 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 333.97 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2861.66 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 221.56 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km |  | CONDUCTOR AAA SQURREL |  | ITEM DELETED: NOT TO BE USED
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km |  | CONDUCTOR AAA WEASEL |  | ITEM DELETED: NOT TO BE USED
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km |  | CONDUCTOR AAA RABBIT |  | ITEM DELETED: NOT TO BE USED
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km |  | CONDUCTOR AAA RACOON |  | ITEM DELETED: NOT TO BE USED
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 51.51 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 201.06 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 1055.83
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 23770.24 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq) | ISI MARK
7130830054 | Bimetallic clamp for VCB | Each | 616.6
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 36110.28 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq) | ISI MARK
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 616.6
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 60086.82 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q) | ISI MARK
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 313.46
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 89510.94 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E | ISI MARK
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 120401.41 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq) | ISI MARK
7130830070 | 0.2 Sq inch ( 200 Sqmm Al.Eq.)(Panther) | Km | 266865.51 | CONDUCTOR ACSR PANTHER 200 sq mm | ISI MARK
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km |  | CONDUCTOR AAA DOG |  | ITEM DELETED: NOT TO BE USED
7130830585 | T-Clamp for Dog Conductor. | Each | 380.53 | T-CLAMPS FOR ACSR CONDUCTOR Dog Condutor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 304.09 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830002 | T-Clamp for Panther Conductor. | Each | 445.33 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 459.86 | Bimetallic clamps for transformer & kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 41.54 | SLEEVE JOINTING ALUMINIUM FOR 0.03 SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 310.74 | SLEEVE REPAIR ALUMINIUM FOR .2 SQ INCH AC
7130840021 | 33 kV Porcelain Lightning Arrestor | Each | 4289.09 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 327.8 | LIGHTNING ARRESTORS 11 KV gapless type.
7130850198 | GI Structure for complete Equipment | Kg | 84.31
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 5000.08 | Transformer mounting 100 x 50 mm channel
7130810224 | Transformer Mounting 75x40 mm Channel | Set | 3645.31
7130850203 | Transformer Mounting with Belting for Addl. X-Arm | No. | 4830.74 | Transformer mounting 100 x 50 mm channel
7130810227 | Bracing Set 4' Centre D.P. | Set | 4047.79
7130810228 | Bracing Set 5' Centre D.P. | Set | 5401.45
7130810229 | Bracing Set 8' Centre D.P. | Set | 4973.68
7130810230 | Bracing Cross Arm for 4 Pole Structures | Set | 10776.49
7130860017 | I-Bolt - 16 mm | No. | 131.84 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 592.97 | STAY SET WITHOUT STAY WIRE 16 mm Paint 11 KV
7130860033 | Stay Set 20 mm (Painted) | Each | 1080.47 | STAY SET WITHOUT STAY WIRE 20 mm (Painted)
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 87273.82 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 88128.62 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 997.81
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 143.69 | EARTHING COIL 8SWG GI WIRE 50 MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 448.38 | Earthing rod 25mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 69873.22 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 69823.35 | G.I. WIRES: - 4.0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 69823.35 | G.I. WIRES: - 5.0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 2238.1
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 1315.11 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 3137.26 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2788.67 | Jointing Kit&HW LT ABC CableStraight Sus
7130880006 | Cable marker for U/G cable | No. | 143.01 | CABLE MARKER FOR U/G CABLE
7130880007 | Pad Connector (for Panther conductor) | No. | 181.84 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 101.61 | Danger boards 33 KV & 11 KV.
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 5709.28 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 7203.73
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 16338.04 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 17116.04 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 60.21 | LT LINE SPACERS
7130890973 | Stainless steel strap with buckle (for installation of Service Distribution Box) | Set | 63.44
7131961526 | Modem (4G) | Nos. | 4665.77 | MODEM
7130893004 | Eye Hook | No. | 237.57 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 3645.31 | 33 KV guarding channel 100x50 mm.
7130810233 | Railway Cross Structures | Set | 19357
7130810235 | Railway Pole Jointing Channel | Set | 1851.8
7131210001 | Panel lndication lamps | Nos. | 135.12
7131210010 | LED 7 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210018 | LED 12 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210019 | LED 14 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210020 | LED 15 Watt lamp with holder | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210021 | LED Lamps with COMPLETE FITTING - 15 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210022 | LED LAMPS WITH COMPLETE FITTING - 20 W | Nos. |  |  |  | ITEM DELETED: NOT TO BE USED
7131210852 | CFL 7 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131210881 | 250 Watt Metal Halide | Each |  | METAL HALIDE LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131220182 | Tube Light Rod (T5 type) | Each |  | LAMPS: -Tube Light (40 Watts.) |  | ITEM DELETED: NOT TO BE USED
7131230003 | 250 Watt Sodium Vapour | Each |  | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER |  | ITEM DELETED: NOT TO BE USED
7131230116 | 250 Watt Mercury Vapour | Each |  | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO |  | ITEM DELETED: NOT TO BE USED
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each |  | S/ V HIGH PRESSURE LAMP 400W 230/250V |  | ITEM DELETED: NOT TO BE USED
7131280006 | CFL 15 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280007 | CFL 20 Watts | Each |  | CFL 20 WATTS LAMP |  | ITEM DELETED: NOT TO BE USED
7131280008 | CFL 23 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280009 | 125 Watt Mercury Vapour | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280010 | Halogen Filament (1000 Watts) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131280012 | Street Light fitting with tube light | Each |  | STREET LIGHT FITTING WITH TUBE LIGHT |  | ITEM DELETED: NOT TO BE USED
7131280013 | Street Light fitting with CFL | Each |  | STREET LIGHT FITTING WITH CFL |  | ITEM DELETED: NOT TO BE USED
7131280014 | HPSV lamp 150 watt | Each |  | HPSV LAMP 150 WATT |  | ITEM DELETED: NOT TO BE USED
7131280015 | HPSV Choke 250 watt | Each |  | HPSV LAMP 250 WATT |  | ITEM DELETED: NOT TO BE USED
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each |  | 150 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each |  | 250 WATT METAL HALIDE HPSV FITTING |  | ITEM DELETED: NOT TO BE USED
7131280882 | CFL 11 Watts | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 1975.28 | ENERGY METER ENECTRONIC 10-60 AMPS | ISI MARK
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for __/110 Volts; __/1 Amps; or __/5 Amps) | Each | 1575300 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 191.63 |  |  | RATE EXCLUDING G.S.T.
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 917.98 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 858.9 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A | ISI MARK
7131300881 | CMRI (Common Meter Reading Instrument) | Each | 28091.6 | Common Meter Reading Instrument CMRI
7131310002 | CT operated electronic static bidirectional meter with DLMS for net metering | Each | 3537.38
7131310005 | CT operated electronic static bidirectional meters with DLMS protocol for net metering | Each | 3433.69
7131310045 | Bidirectional Meter 1 phase for Solar Roof Top | Each | 1216.2
7131310040 | Bidirectional Meter 3 phase for Solar Roof Top | Each | 2533.76
7131310013 | 3 Ø 4 Wire 0.5S, 5 Amp. Bulk consumer meter | Each | 5411.58 | HT TRIVECTOR METER 5 AMPS | ISI MARK
7131310015 | CT operated electronic static meters with AMR (Composite Unit) with LTCTs / Modem / Meter / Meter Box. | Each | 15351.14 | ELECTORNIC LTCT METER 3X4 100/5 A | ISI MARK
7131310033 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | Each | 4787.15 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310034 | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category B | Each | 4787.15 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR | ISI MARK
7131310035 | 3 Ø 4 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 27140 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310036 | 3 Ø 3 Wire 0.2S, 1 Amp. bulk consumer meter | Each | 22450.99 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC ( | ISI MARK
7131310042 | 3 Ø 4 Wire 0.2S 5A bulk consumer meter | Each | 29182.22 |  | ISI MARK
7131397678 | Test terminal Box (TTB) | Each | 2223.5 | TTB
7131310997 | CT operated electronic static bidirectional meters with DLMS Protocol. | Each | 2075.36 | 3 PHASE 4 WIRE LTCT OPERATED METER | ISI MARK
7131320009 | Digital Multimeter Electronic Type | Nos. | 3748.4 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) Digital | Nos. | 4730.03 |  |  | RATE EXCLUDING G.S.T.
7131324780 | Megger 500 V | Nos. | 4498.07
7131324806 | Megger up to 2.5 kV | Nos. | 6779.28 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 9186.23
7131334001 | Set of 3 O.C. relays + 1 E/F instantaneous high set feature numerical type | Nos. | 8466.5 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C. + 1 earth fault relay without numerical instantaneous high set feature | Nos. | 8608.43 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1339.85
7131300008 | Auxiliary Relay | Nos. | 3486.52
7131300009 | Electrically Reset type Master Trip relay | Nos. | 3891.96
7131300010 | SCADA Compatible Relay (As per IEC 107/IEC61850 protocol) | Nos. | 40195.64
7131338004 | Transformer Oil Dielectric Breakdown testkit | Nos. | 76047.97 |  |  | RATE EXCLUDING G.S.T.
7131338025 | Neon tester | Nos. | 72.35 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 310.89
7131387502 | Thermometer (Wall Mounted) | Nos. | 615.08 | THERMOMETER (WALL MOUNTED)
7131390014 | Earthing Coil for messenger wire | Nos. | 249.92
7131390015 | Anchor sleeve for messenger wire | Nos. | 43.21
7131390016 | Universal hook & Bolts & nuts | Nos. | 605.45
7131820031 | LT Single Phase MCB 5 Amps. | Each | 131.01
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 131.01 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 555.21
7131820034 | LT Three Phase MCB 32 Amps. | Each | 555.21
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 3698.38
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 4007.12
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 4007.12
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2927.84
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 6704.05 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900005 | Locally fabricated - 3 Phase fuse units 150 Amps. (Robust fuse for circuit base). | Each | 988.84 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 9.12 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 366.33 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 563.19 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 15.63 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 16.94 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 361.12 | H.R.C. FUSE UNITS: -100 Amps.
7131900807 | H.R.C. Fuse 100 Amps. | Each | 140.8 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 907.36 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 1003.84 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 1248.1 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 1248.1 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 10 SWG
7131900974 | T.C. Fuse Wire 8 SWG | Kg | 1209.5 | FUSE WIRE TINNED COPPER 8 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 57.94 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 114.49 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 33.11 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 306.25 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 673.19 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 1235.82 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920001 | Load break switches only without panel | Unit | 53857.26 | LOAD BREAK SWITCH WITHOUT PANEL
7131920002 | Load break switches with panel | Unit | 117398.63 | LOAD BREAK SWITCH WITH PANEL
7131920003 | 3 Way Load break switch | Unit | 379797.6 | 3 WAY LOAD BREAK SWITCH
7131920112 | 11 kV Kiosk VCB | Each | 420462.61 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 960.3 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 2305.88 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 4460.3 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 6261.77 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 8495.6 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 12832.35 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  |  | 51.2435
7131930109 | 33 kV ; 600 Amps with earth switch. | Each |  | 33 KV 600 AMPS WITH EARTH SWITCH ISOLATO |  | ITEM DELETED: NOT TO BE USED
7131930221 | 11 kV Porcelain A.B. Switch | Each | 10471.34 | AB Switch with complete fitting 11 KV
7131930321 | 33 kV Porcelain A.B. Switch | Each | 23249.28 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1237.27 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 3310.46 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 26094.57 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 45159.49 | 33 KV Isolator 800A without earth switch
7131931091 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure | Set | 34350.79
7131931095 | Mounting GI structure for above isolator | Set | 14583.18
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 3082.2 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 29280.91 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 29280.91
7131940871 | Indoor Type Automatic Control Unit along with APFC Relay | No. | 57681.32
7131941762 | 11 kV VCB without control panel & CT's. | Each | 154192.41 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 280899.21 | 33KV VCB FOR 30 VOLT DC
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1331.11 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1603.46 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 50551.61
7131950016 | 11 kV Sectionalizer. | Each | 446178.57
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 18891.13 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 23614.9 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 47227.82 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 40524.33 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131950208 | SMC LT Distribution Box for 100 kVA Distribution Transformer | Each | 15533.64
7131950209 | SMC LT Distribution Box for 315 kVA Distribution Transformer | Each | 22892.01
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 28893.09 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 31900.75 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 28124.69 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 29632.55 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960010 | 11 kV Control & Relay Panel for Capacitor Bank | Each | 91055.26
7131960520 | 2 Feeder Control (Static Relays) | Each | 42122.51 | 11KV MULTICIRCUIT (2F) CONTROL PANELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 42392.8 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 43018.74 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm; 3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 224.48
7132004003 | Hack saw frames + B185 | Nos. | 143.91
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 15.1
7132011171 | Cable Cutter | Nos. | 530.56
7132013331 | Discharge Rod | Nos. | 539.91 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 3698.44
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 1436.34
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 444.41
7132061858 | Combination Plier / Cutting Plier | Nos. | 247.05 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 79.9 | SCREW DRIVER 250MM
7132072004 | Screw driver 200 mm | Nos. | 74.83 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 69.76 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. |  | SCREW DRIVER INSULATED 255 MM |  | ITEM DELETED: NOT TO BE USED
7132074032 | Ring Spanners (6x7,8x9,10x11,12x13, 14x15,16x17,18x19,20x22x,21x23, 24x27,25x28,30x32) | Set. | 1740.05 | RING SPANNER
7132074033 | Tube Spanners | Set. | 719.1
7132074034 | Double end spanner (6x7,8x9,10x11, 12x13,14x15,16x17,18x19,20x22x, 21x23,24x27,25x28,30x32) | Set. | 823.1 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 533.93
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F & tommy Bar) | Set. | 1585.32 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1321.44
7132088615 | Pipe Wrench 18 inches size | Nos. | 725.21
7132200014 | 1089 kVAR, 12.1 kV, 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kVAR + 726 kVAR 12.1 KV. Bank shall be complete with Capacitor units of 121 kVAR at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin / Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | Each | 174623.28 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 2117.99 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 4234.66 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 5088.22 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 8444.12 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 230907.67 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each |  | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 25KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 63KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 100KVA 11/0.43KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each |  | TRANSFORMER 200KVA 11/0.4KV FOUR STAR |  | ITEM DELETED: NOT TO BE USED
7132210012 | 315 kVA (CEA Design) Copper wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | XMER 315KVA 11/0.43KV CEA REG. CU WOUND |  | ITEM DELETED: NOT TO BE USED
7132210015 | 500 kVA [CEA Design] Copper Wound ISI Marked, 11/0.433 kV Distribution Transformer having energy efficiency level '2' | Each |  | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer |  | ITEM DELETED: NOT TO BE USED
7132210106 | 0.2% Reactor suitable for 363 kVAR step | Set | 8479.9
7132210108 | 0.2% Reactor suitable for 726 kVAR step | Set | 10352.43
7132210215 | 50 kVA (Copper winding) 33/0.4 kV | Each | 251830.58 | TRANSFORMER 33/.4KV 50KVA
7132220091 | Power Transformer 1600 kVA | Each | 1500128.26 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 33/11 KV 3150 kVA | Each | 4456033.02 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 33/11 KV 5000 kVA | Each | 6078909.05 | TRANSFORMER 33/11KV 5 MVA POWER
7132220092 | Power Transformer 33/11 KV 8000 kVA | Each | 8585074.33 | TRANSFORMER 33/11KV 8 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 267615.99 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 527.46 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 247011.43 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 313.29 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 306.8 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 306.8 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1-1A | No. | 765668.4 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 20221.34 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1-1A | No. | 379690.42 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1-1A | No. | 578052.83 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1-1A | No. | 966723.73 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1-1A | No. | 695772.88 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1-1A | No. | 779566.92 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 47130.87
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 107545.2 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 18154.3 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 15178.97 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132200005 | 11 kV C.T. 500-250/5-5 Amps. | Each | 20686.37
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 24806.55 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5-5) Amps oil filled | Each | 25114.47 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each |  | 33KV CT's (100-50/5)A oil filled OD Type |  | ITEM DELETED: NOT TO BE USED
7132230330 | 132 kV C.T. 100-50/1-1A | No. | 730790.17 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1-1A | No. | 541345.24 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1-1A | No. | 347506.34 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A |  | ITEM DELETED: NOT TO BE USED
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 46126.52 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A |  | ITEM DELETED: NOT TO BE USED
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 47126.62 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 42464.01 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A |  | ITEM DELETED: NOT TO BE USED
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 46601.35 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230538 | 11 kV CTPT Unit 50/5 A | Each | 42223.13 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230543 | 132 kV C.T. 100/1 A | No. | 612282.8
7132230544 | 132 kV C.T. 200/1 A | No. | 531661.4
7132230545 | 220 kV C.T. 800/1 A | No. | 641365.19
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 79231.77 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 103432.83 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A |  | ITEM DELETED: NOT TO BE USED
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 86517.16 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each |  | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A |  | ITEM DELETED: NOT TO BE USED
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 78269.35 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 79399.73 | OIL IMM 3 PH CTPT UNITS 33 KV-100 & 200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 79399.73 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230458 | 33 kV CTPT Unit 400/5A | Each | 75595.51 | OIL IMMERSED 3 PHASE CTPT UNITS 400/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 105928 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230411 | 33 kV CTPT Unit 300/5A | Each | 79399.73
7132230471 | 11 kV 3 PH Residual Voltage Transformer | Each | 41166.48
7132230473 | 11 kV PT Station Type | No. |  |  |  | ITEM DELETED: NOT TO BE USED
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 14164.44 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 22774.85 | VOLTAGE TRANSFORMER 33 KV / 110 VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 466237.64 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 843207.67 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132404015 | Safety belts | Nos. | 697.82 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 162.57 | SAFETY HELMETS
7132404366 | Battery | No. | 67787.02 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 197.85 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 3297.37 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406793 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 4124.76
7132406795 | Pilfer proof Single Compartment SMC meter box for LTCT meters 150/5A with CT | Each | 4896.43
7132406794 | Pilfer proof Single Compartment SMC meter box for LTCT meters 300/5A with CT | Each | 4470.9
7132406425 | Universal Meter Box for HT meters. | Each | ITEM DELETED | Universal Meter Box for HT meters. |  | ITEM DELETED: NOT TO BE USED
7132404529 | Sheet Metal deep drawn HT Meter Box | Each | 4765.89
7132406791 | Sheet Metal deep Drawn Meter Box for LTCT operated meter | Each | 6875.8
7132406721 | CT operated electronic static meters with DLMS. | Each | 3089.55 | LTCT METER WITH DLMS | ISI MARK
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 1675.6 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 6562.35 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 892.42 | RAIN COATS WITH HOODS |  | RATE EXCLUDING G.S.T.
7132427635 | Gum Boots | Nos. | 594.9 | GUM BOOTS |  | RATE EXCLUDING G.S.T.
7132438002 | Silica gel | Kg | 206.57 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 5.84 | POLYCARBONATE SEAL
7132444006 | Holographic Sticker Seal | Each | 2.78
7132444007 | Grounding Sticks (Galvanised Earthing Rods 25 mm, 3 Mtr. long) | Set. | 1028.41
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 6133.6 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 413.82
7132457795 | EHV Gr-I TRANSFORMER OI In Barrel | KL | 89113.6 | TRANSFORMER OIL In Tanker/barrel
7132457800 | EHV Gr-I TRANSFORMER OIL In Tanker | KL | 83343.4 | TRANSFORMER OIL In Tanker/barrel
7132494004 | Fabricated Transformer Oil Storage Tank (10 Kl Capacity) | No. | 438497.86 | Fabricated Transformer Oil Storage Tank
7132459005 | Poly Carbonate seal double anker type | Each | 7 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | ITEM DELETED | HDPE PIPE 200MM ID; 240MM OD |  | ITEM DELETED NOT TO BE USED
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 560.41 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 17700 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 393.26
7132479016 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 153.92 |  |  | RATE EXCLUDING G.S.T.
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 17.63 | PVC INSULATION TAPES 19 MM WIDE AND IN R |  | RATE EXCLUDING G.S.T.
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 83.43 |  |  | RATE EXCLUDING G.S.T.
7132478004 | Tong tester Digital (1000 A, 500 V) with associated accessories | Nos. | 1913.64 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 786.36 | HAND TORCH 5 CELLED
7132478012 | Hand Torch 3 cell | Nos. | 515.55 | HAND TORCH 3 CELLED
7132470004 | Cotton Waste | Kg | 84.11 |  |  | RATE EXCLUDING G.S.T.
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 5868.51 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 75.51 |  |  | RATE EXCLUDING G.S.T.
7132490053 | Bitumen compound | Kg | 135.92
7132498006 | River sand | Cmt | 737.1 | RIVER SAND
7130310027 | 11 kV Covered Conductor 50 Sqmm XLPE insulation | Mtr. | 354.22 | 11KV COVERED CONDUCTOR XLPE 50SQMM
7130310029 | 11 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 394.13 | 11KV COVERED CONDUCTOR XLPE 70SQMM
7130310002 | 11 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 437.83 | 11KV COVERED CONDUCTOR XLPE 99SQMM
7130310047 | 33 kV Covered Conductor 157 Sqmm XLPE insulation | Mtr. | 719.53 | 33KV COVERED CONDUCTOR XLPE 157SQMM
7130310048 | 33 kV Covered Conductor 241 Sqmm XLPE insulation | Mtr. | 856.83 | 33KV COVERED CONDUCTOR XLPE 241SQMM
7130310045 | 33 kV Covered Conductor 70 Sqmm XLPE insulation | Mtr. | 532.63 | 33KV COVERED CONDUCTOR XLPE 70SQMM
7130310046 | 33 kV Covered Conductor 99 Sqmm XLPE insulation | Mtr. | 582.21 | 33KV COVERED CONDUCTOR XLPE 99SQMM
ACCESSORIES FOR COVERED CONDUCTOR :-
7130320050 | (i) Tension / anchoring Clamp with tracking protection IPC | No | 1218.98 | Tension/anchoring Clamp with tracking protection
7130320051 | (ii) Alignment tie (non-metallic) | No | 488.82 | Alignment tie (non-metallic)
7130320052 | (iii) Mechanical conductor with heat shrunk sleeve for bare to covered | No | 1194.48 | Mechanical conductor with heat shrunk sleeve for bare to covered
7130320054 | (iv) IPC for Networking / Branching / Looping CC to CC | No | 1071.97 | IPC for Networking / Branching / Looping CC to CC
7130320055 | (v) IPC with Aluminium Bail for earthing | No | 1255.74 | IPC with Aluminium Bail for earthing
7130320056 | (vi) Mid span joint | No | 673.81 | Mid span joint
7130320057 | (vii) IPC with Aluminium Bail & Transformer Tap (Line this) | No | 1255.74 | IPC with Aluminium Bail & Transformer Tap (Line this)
7130320058 | (viii) Heat Shrinkable End Cap | No | 24.5 | Heat Shrinkable End Cap
7130320059 | (ix) Termination kit / Lug for Transformer Connection | No | 673.81 | Termination kit/Lug for Transformer Connection
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 24159.44 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 37310.86 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 233847.1 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 336819.47 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | ISI MARK
7131310168 | Spot Billing Machine | Each | 13938.4
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 11 kV CTPT Unit 200/5 Amp | Each | 44511.97 |  |  | ITEM DELETED EARLIER, RE-ADDED
7132230403 | 11 kV CTPT Unit 100/5 Amp | Each | 40501.33
7131900012 | C&R Panel with 3 O/C + 1 E/F relay and Master Trip | Each | 50976
7131900014 | Transformer Auxiliary panel with auxiliary protection relay | Each | 12797.78
7131900015 | 33 kV + 11 kV Transformer Protection Panel (including Transformer auxiliary panel) | Each | 55814
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 42819.58
7130870040 | G.I.Strip 25x3 mm | Kg | 88.08
7130640039 | M.S.Strip 25x3 mm. (0.6 kg/Mtr.) | Kg | 42.63 | M.S.Strip 25x3 mm.
7132444008 | Numerical Poly Carbonate seals | No | 10.76
7130820013 | 33 kV Polymer Disc Insulator (45 kN) | No | 187.29
7131930110 | D.O.Fuse Polymer unit 11 kV | Each | 1506.92
7131930111 | D.O.Fuse Polymer unit 33 kV | Each | 2156.64
7130800001 | PCC Pole 200 kG; 9.0 Mtr. Long | Each | 3195.95 |  |  | Rate are inclusive of all T&P and labour charges
7130800002 | PCC Pole 365 kG; 11 Mtr. Long | Each | 7887.84 |  |  | Rate are inclusive of all T&P and labour charges
7130820001 | 11 kV Polymer Post Insulator | Nos. | 252.87
7130820002 | 33 kV Polymer Post Insulator | Nos. | 963.99
7130820020 | Silicon rubber composite insulator / 11 kV 45 kN Polymeric Insulator | Nos. | 111.39
7131930220 | Polymer A.B.Switch with complete fitting 11 kV | Each | 7998.21
7131930320 | Polymer A.B.Switch with complete fitting 33 kV | Each | 18927.97
7130800032 | 200 Kg 8.0 Meter long PCC Pole | No | 2673.36 |  |  | Rate are inclusive of all T&P and labour charges
7130311023 | 2.5 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 33.24 | 2.5 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311024 | 4.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 39.88 | 4.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311025 | 6.0 sqmm. Twin Core PVC insulated single phase armoured service Cable | Per Mtr. | 58.16 | 6.0 sqmm 2C 1ɸ Armour PVC insulated service Cable
7130311026 | 6.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 69.79 | 6.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311027 | 8.0 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 84.75 | 8.0 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311028 | 10 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 101.37 | 10 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311029 | 16 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 132.96 | 16 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311030 | 25 sqmm. Four Core PVC insulated three phase Armoured service Cable | Per Mtr. | 169.51 | 25 sqmm 4C 3ɸ Armour PVC insulated service Cable
7130311085 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 258498.93 | 240 sq.mm Single Core PVC Sheathed Unarmoured Cables
7132210017 | 16 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 77310.58 | XMER 16KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210018 | 25 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 65016.7 | XMER 25KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210019 | 63 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 125345.25 | XMER 63KVA 11/0.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210020 | 100 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 164821.1 | XMER 100KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132210021 | 200 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 352684.76 | XMER 200KVA 11/.4KV ENERGY EFFI. LEVEL2 | ISI MARK
7132220081 | 315 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 1071277.58 |  | ISI MARK
7132220082 | 500 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (Without Box) | Each | 1521670.31 |  | ISI MARK
7132210022 | 25 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 78621.18
7132210023 | 63 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 135219.73
7132210024 | 100 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 165773.86
7132210025 | 200 kVA, Aluminium wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 354119.68
7132210027 | 315 kVA, Copper wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box) | Each | 965414.75
7132210028 | 25 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 82528.82
7132210029 | 63 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 148218.56
7132210030 | 100 kVA Aluminium Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With Secondary Terminal Box - extended LT bushing | Each | 192133.46
7132220085 | 315 kVA Copper Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With HV & LV side Box) | Each | 1087040.36
7132220086 | 500 kVA Copper Wound ENERGY EFFICIENCY LEVEL-1 (As per IS:1180 amendment 4), I.S.I. MARKED 11/0.4 kV DISTRIBUTION TRANSFORMER (With HV & LV side Box) | Each | 1547700.56
7130640008 | RCC Block (with 6 mm MS Bar) | Each |  |  |  | ITEM DELETED: NOT TO BE USED
7130300055 | Round Shape RCC Base Plate(with 6mm MS Bar) | Each | 173 |  |  | Rate are inclusive of all T&P and labour charges
7130300056 | Square Shape RCC Base Plate(with 6mm MS Bar) | Each | 293 |  |  | Rate are inclusive of all T&P and labour charges
7131210011 | LED 9 Watt Lamp (without holder) | Each | 77 | LED 9 W lamp with holder
7131210009 | LED Tube Light, 20 Watt | Set | 242.01 | LED Tube Light, 20 Watt
7131210030 | 18 W LED Street Light complete set | Set | 2491.08 | 18 W LED Street Light complete set
7131210031 | 35 W LED Street Light complete set | Set | 3217.96 | 35 W LED Street Light complete set
7131210032 | 70 W LED Street Light complete set | Set | 4552.2 | 70 W LED Street Light complete set
7131210033 | 110 W LED Street Light complete set | Set | 6186.43 | 110 W LED Street Light complete set
7131210034 | 190 W LED Street Light complete set | Set | 10910.5 | 190 W LED Street Light complete set
7131210035 | 190 W LED Flood Light complete set | Set | 10585.25 | 190 W LED Flood Light complete set
7131210036 | 110 W LED Flood Light complete set | Set | 7069.16 | 110 W LED Flood Light complete set
7131210023 | LED Lamps with complete fitting-24 W | Nos. |  | 24 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210024 | LED Lamps with complete fitting-48 W | Nos. |  | 48 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131210025 | LED Lamps with complete fitting-60 W | Nos. |  | 60 W LED Lamps with complete fitting |  | ITEM DELETED: NOT TO BE USED
7131941763 | 3 Way RMU, 2OD + 1VL, One Incomer + One Breaker + One Outgoing, 350 MVA, 650 Amps. | Unit | 939353.2 | 11 kV RMU 3 WAY,2 OD+1 VL, 350 MVA, 650 A.
7131941764 | 4 Way RMU, 2OD + 2VL, (One Incomer + Two Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1334322.01 | 11 kV RMU 4 WAY,2 OD+2 VL, 350 MVA, 650 A.
7131941765 | 5 Way RMU, 2OD + 3VL, (One Incomer + Three Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 1722255.71 | 11 kV RMU 5 WAY,2 OD+3 VL, 350 MVA, 650 A.
7131941766 | 6 Way RMU, 2OD + 4VL,(One Incomer + Four Breakers + One Outgoing), 350 MVA, 650 Amps. | Unit | 2110189.41 | 11 kV RMU 6 WAY,2 OD+4 VL, 350 MVA, 650 A.
7131941767 | 1OD for RMU | Unit | 337998.09 | 1OD for RMU
7131941768 | 1VL for 350 MVA, 650 Amps RMU | Unit | 394968.81 | 1VL for 350 MVA, 650 Amps RMU
7132230028 | Indoor Type 33 kV Metering Cubical CTPT Unit 10/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 10/5A CT:PT CUBICAL UNIT
7132230029 | Indoor Type 33 kV Metering Cubical CTPT Unit 25/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 25/5A CT:PT CUBICAL UNIT
7132230030 | Indoor Type 33 kV Metering Cubical CTPT Unit 200/5 A | Each | 247011.43 | INDOOR TYPE 33 KV 200/5A CT:PT CUBICAL UNIT
7132230031 | Indoor Type 11 kV Metering Cubical CTPT Unit 10/5 A | Each | 117805.45 | INDOOR TYPE 11 KV 10/5A CT:PT CUBICAL UNIT
7132230020 | Indoor Type 11 kV Metering Cubical CT-PT Units 15/5 A | Each | 117805.45 | Indoor Type 11kV 15/5A CTPT Cubical Unit
7132230010 | Indoor Type 11 kV Metering Cubical CTPT Unit 25/5 A | Each | 117805.45 | INDOOR TYPE 11 KV 25/5A CT:PT CUBICAL UNIT
7132230027 | Indoor Type 11 kV 50/5 A Metering Cubical CT-PT Units | Each | 117807.48 | Indoor Type 11kV 50/5A CTPT Cubical Unit
7131980004 | (0+1) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH ONE 630 A LOAD BREAK SWITCH. | No. | 285484.83
7131980005 | (0+3) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH THREE 630 A LOAD BREAK SWITCHES. | No. | 527899.18
7131980006 | (0+4) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR 630 A LOAD BREAK SWITCHES. | No. | 640487.09
7131980007 | (0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH FOUR NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER IN BETWEEN AFTER ISOLATOR. | No. | 1020610.69
7131980008 | (0+2)+BC+(0+2)+BC+(0+2) TYPE - MEANS 11 KV GAS (SF6) INSULATED RMU WITH SIX NOS. 630 A LOAD BREAK SWITCHES AND ONE BUS COUPLER WITH LBS IN BETWEEN AFTER ISOLATOR. | No. | 1614068.62
7131941001 | Feeder Remote Terminal Unit (FRTU) with accessories Multifunction Transducer (MFT), Contact Multiplication Relay (CMR), Heavy Duty Relay & software. | No. | 105881.18
7131941002 | Compact arrangement of RMU+FRTU+ LT Distribution Box in a closed chamber for 11/0.433 kV Distribution sub-station (excluding Distribution Transformer) with Transformer in top & RMU+FRTU+ LT Distribution Box in bottom, compatible upto 650 kVA. | No. | 1553775.07
7131941003 | Compact arrangement of RMU+FRTU+ LT Distribution Box in a closed chamber for 11/0.433 kV Distribution sub-station (excluding Distribution Transformer) with Transformer in top & RMU+LT Distribution Box in bottom, compatible upto 650 kVA. | No. | 1265446.31
7131980001 | 12 kV, Outdoor type Vacuum Capacitor switches | No. | 83678.8
7131920028 | AC Distribution board for AC/DC Supply | No. | 12330.35
7132486843 | Chem Rod Earthing electrode (Chemical Earthing) [As per specification given in Schedule-C-20] | Job | 9170.44 |  |  | RATE EXCLUDING G.S.T.
7130840003 | Surge Arrestor | No. | 1109.72
7131950396 | Ground connection for Messenger Wire | No. | 168.6
7132406800 | 33/11 kV S/S (Name Plate) Board | Job | 10253.32
7131210840 | 11 kV Fault Passage Indicator for Overhead line | No. | 17780.12 |  |  | RATE EXCLUDING G.S.T.
7132455003 | SMC Meter Board 350x200x40 mm (minimum) thickness 2.5 mm | No. | 162.74 | SMC Meter Board 350x200x40 mm, thickness 2.5 mm
7132455004 | SMC Board 200x150x40 mm (minimum) thickness 2.5 mm | No. | 127.87 | SMC Board 200x150x40 mm thickness 2.5 mm
7131920004 | Piano type ISI mark 250V/5A switch. | No. | 13.82 | Piano type ISI mark 250V/5A switch.
7131920005 | 250V/5A ISI mark 3 pin Socket | No. | 34.55 | 250V/5A ISI mark 3 pin Socket
7131920006 | 250V/5A ISI mark holder. | No. | 20.73 | 250V/5A ISI mark holder.
7131390482 | Earthing terminal (having suitable size of 10 mm Dia GI bolt with 3 nos. nuts & washers) along with Staples/ Nut-Bolts/ Nails | No. | 58.12 | Earth terminal(10mm Dia GI bolt with 3 no) nuts & washers) along with Staples/ Nut-Bolts/ Nails
7130310081 | Internal wiring using 1.5 sqmm copper multistrands PVC insulated ISI marked cable (Average cable length 6 Mtr.) | Mtr | 10.54 | 1.5 sqmm copper multistrand PVC cable
7132461006 | 25 mm Dia PVC pipe or equivalent for internal house wiring (3 Mtr) | Feet | 6.57 | 25 mm Dia PVC pipe or equivalent (3 Mtr)
7132498054 | Bhatta brick | No. | 6.57 | Bhatta brick
7131397216 | Meter Sealing Wire | Kg | 244.83
7132010551 | Hand Operated type 25 sq.mm. to 400 sq.mm Crimping Tool | No. | 9846.82
7132010552 | Hydraulic type Crimping Tool with suitable Dies for crimping Lugs of size up to 400 sq.mm. | Set | 12561.71
7132478005 | RECHARGEABLE L.E.D. HAND TORCH | No. | 865.13 | RECHARGEABLE L.E.D. HAND TORCH
7132089020 | Cable separator in RCC Pipe with Angle Cross of 50x50x6 mm Angle @ 2 No. in one pipe | No. | 735.03 | Cable separator in RCC Pipe with 50x50x6 mm Angle
7132200004 | 11 kV Capacitor Unit with Expulsion Tube | Each | 139.58 |  | (cost per kVAR)
7131310032 | ABT Meter Accuracy class: 0.2s, C.T. Ratio: _/1A, P.T.Ratio: _/110V | No. | 313249.88
7131310048 | 3 Ø 4 Wire ABT meter | No. | 286843.81
7131310049 | 3 Ø 3 Wire ABT meter | No. | 286843.81
| Cost of Galvanization | MT | 26773.02
7132401667 | Office Almirah Storwel plain with 4 shelves 78''x36''x19'' | No. | 15340
7132401205 | Office Almirah Storwel minor plain 50''x30''x17'' | No. | 7552
7132409830 | Office Chair model CH-7 cane seat & back with full arms rest | No. | 4720
Office Table
7132476013 | 5'x3.5'x2.5' | No. | 11918
7132476792 | Model T-8 4'x2' | No. | 16732.4
7132476797 | Model T-9 4.5'x2.25' | No. | 10620
7132476795 | Ex. Table Model T-104 66''x36'' | No. | 25960
7132409025 | Computer Table | No. | 9912
7132409061 | Computer Chair | No. | 5900
7132401672 | Small almirah 50", 20 SWG Sheet | No. | 8024
7132476014 | Office Table 4'x2.5' | No. | 8968
7132409815 | Chair | No. | 2301
7132409819 | Officer Chair | No. | 2832
Steel Rack
7132401669 | 78''x36''x18'' (Heavy) | No. | 7080
7132476016 | 72''x36''x15'' (Heavy) | No. | 4484
7132476799 | 59''x39''x18'' | No. | 5900
7132499008 | PC with Monitor : i3; 4th Gen, 4 GB RAM, 1TB HDD, 18.5” Display (Monitor), Windows 8 | Set | 61950
7132499023 | LAPTOP : i5; 8th Gen, 8 GB RAM, 1TB HDD, Win 10 OS, MS-Office-10 Home Edition, 13.3” Display, | No. | 68440
Laser Printer : B/W
7132499029 | Speed 12 PPM | No. | 17464
7132499044 | Speed 28 PPM (Multi function) | No. | 40120
7132420412 | Fax Machine with print and copy capabilities. | No. | 10620
7132488810 | Photo copier | No. | 48999.5
7132531017 | Scanner : 2400 x 4800 dpi, | No. | 8848.82
7132486006 | Water Purifier | No. | 10785.2
7132486195 | Water Cooler (80 Ltr) | No. | 41300
7132401202 | Air Cooler | No. | 6490
7132420160 | Ceiling Fan (48") [BEE 5 star rating] | No. | 2080.01
7132486151 | Wall Coffer | No. | 11800
7131880133 | Air Conditioner 2 Ton 4 Star (Split) | No. | 48527.5
7131880134 | Air Conditioner 1.5 Ton 4 Star (Split) | No. | 36119.07
7132486004 | UPS 600 VA | No. | 2006
EHV- Gr-1, TRANSFORMER OIL
7130572150 | Contaminated Oil | Ltr | 50.01 |  |  | RATE EXCLUDING G.S.T.
ALUMINIUM ITEMS
7130570050 | Aluminium | Kg | 102 |  |  | RATE EXCLUDING G.S.T.
7130570160 | ACSR Conductor | Kg | 167.7 |  |  | RATE EXCLUDING G.S.T.
7130570925 | Aluminium UG Cable | Kg | 83 |  |  | RATE EXCLUDING G.S.T.
7130570055 | Aluminium Wire in pieces | Kg | 88 |  |  | RATE EXCLUDING G.S.T.
7130570055 | Released Aluminium windings from failed Distribution Transformers | Kg | 94 |  |  | RATE EXCLUDING G.S.T.
7130570185 | Insulated wire / cable aluminium Scrap | Kg | 150 |  |  | RATE EXCLUDING G.S.T.
COPPER ITEMS
7130570167 | Copper Wire | Kg | 794 |  |  | RATE EXCLUDING G.S.T.
7130570167 | Released Copper Windings from failed Distribution Transformers | Kg | 794 |  |  | RATE EXCLUDING G.S.T.
IRON ITEMS
7130570145 | Rail Pole, H-Beam | Kg | 39.11 |  |  | RATE EXCLUDING G.S.T.
7130570200 | Cross Arms, Clamps , MS Scrap etc. | Kg | 42.73 |  |  | RATE EXCLUDING G.S.T.
7130570910 | Barbed Wire / Ground Wire | Kg | 57.51 |  |  | RATE EXCLUDING G.S.T.
7130560870 | TRANSFORMER EMPTY TANKS OF DIFFERENT CAPACITY | Kg | 41 |  |  | RATE EXCLUDING G.S.T.
7130500153 | BROKEN STEEL FURNITURE | Kg | 15 |  |  | RATE EXCLUDING G.S.T.
7130570915 | SCRAP WOODEN FURNITURE | Kg | 6.93 |  |  | RATE EXCLUDING G.S.T.
7130560150 | Empty barrel of 210 litres capacity 200/210 Ltrs. | No. | 287 |  |  | RATE EXCLUDING G.S.T.
7130570205 | Lead | Kg | 121 |  |  | RATE EXCLUDING G.S.T.
7130570125 | Brass | Kg | 443.45 |  |  | RATE EXCLUDING G.S.T.
CTs & PTs
7130530601 | 11 KV CT | No. | 3319.14 |  |  | RATE EXCLUDING G.S.T.
7130530602 | 33 KV CT | No. | 5163.1 |  |  | RATE EXCLUDING G.S.T.
7130530604 | 11 KV PT | No. | 4022.91 |  |  | RATE EXCLUDING G.S.T.
7130530604 | 33 KV PT | No. | 5368 |  |  | RATE EXCLUDING G.S.T.
7130530608 | CT/PT Unit Srap 11 kV | No. | 4425.52 |  |  | RATE EXCLUDING G.S.T.
Energy Meter
7130570230 | Energy Meter (Electro-mech) Single Phase | Kg | 62.9 |  |  | RATE EXCLUDING G.S.T.
7130570230 | Energy Meter (Electro-mech) Three Phase | Kg | 62.9 |  |  | RATE EXCLUDING G.S.T.
7130500152 | Single/Three Phase Electronic Meters | Kg | 99.5 |  |  | RATE EXCLUDING G.S.T.
Scrap Distribution Transformer of Aluminium Winding (without oil)
7130530611 | 16 kVA | Each | 13101 |  |  | RATE EXCLUDING G.S.T.
7130530613 | 25 kVA | Each | 18221 |  |  | RATE EXCLUDING G.S.T.
7130530615 | 63 kVA | Each | 25811 |  |  | RATE EXCLUDING G.S.T.
7130530616 | 100 kVA | Each | 34504 |  |  | RATE EXCLUDING G.S.T.
7130530619 | 200 kVA | Each | 71201 |  |  | RATE EXCLUDING G.S.T.
7130530633 | 315 kVA (Copper Wound) | Each | 225100 |  |  | RATE EXCLUDING G.S.T.
7130530625 | 500 kVA (Copper Wound) | Each | 276315 |  |  | RATE EXCLUDING G.S.T.
7130530611 | Transformer Scrap three Phase 16 kVA Alum. Winding | Each | 14300 |  |  | RATE EXCLUDING G.S.T.
7130530638 | Transformer Scrap Single Phase 16 kVA Copper Winding | No. | 39500 |  |  | RATE EXCLUDING G.S.T.
7130530217 | 33/0.4 KV 63 KVA Transformer Copper Wound | No. | 75506 |  |  | RATE EXCLUDING G.S.T.
7130530223 | 33/0.4 KV 100 KVA Transformer Copper Wound | No. | 659111 |  |  | RATE EXCLUDING G.S.T.
7130500084 | HT Metering Cubicle, Distribution Boxes, feeder piller boxes etc. | Kg | 15 |  |  | RATE EXCLUDING G.S.T.
7130570065 | Automobile parts scrap | Kg | 100 |  |  | RATE EXCLUDING G.S.T.
7130578361 | Pick up Mahindra | No. | 40000 |  |  | RATE EXCLUDING G.S.T.
7132220002 | 3150 kVA, 33/11 kV INDOOR TYPE POWER TRANSFORMER Oil Cooled with Off Circuit Tap Changer with Primary and secondary terminal Box type | Each | 4244979.57 |  |  | RATE EXCLUDING G.S.T.
7132220006 | 5000 kVA, 33/11 kV INDOOR TYPE POWER TRANSFORMER Oil Cooled with Off Circuit Tap Changer with Primary and secondary terminal Box type | Each | 5791627.21 |  |  | RATE EXCLUDING G.S.T.
33 kV Compact Ring Main Unit (RMU) [VCB/SF6 Type] with Aluminium Bus-bar
7131941004 | 3 Way RMU, 2LBS + 1VCB, One Incomer + One Breaker + One Outgoing, SF6 gas, 630 Amps, without FRTU | Unit | 3093346.28 |  |  | RATE EXCLUDING G.S.T.
7131941005 | 4 Way RMU, 2LBS + 2VCB, One Incomer + Two Breakers + One Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 4460868.09 |  |  | RATE EXCLUDING G.S.T.
7131941006 | 3 Way RMU, 3LBS, One Incomer + Two Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 2878364.68 |  |  | RATE EXCLUDING G.S.T.
7131941007 | 4 Way RMU, 4LBS One Incomer + Three Outgoing, SF6 gas, 630 Amps., without FRTU | Unit | 3855336.6 |  |  | RATE EXCLUDING G.S.T.
33 kV JOINTING KIT :-
7130352011 | 33 kV End terminating jointing kit TOUCH PROOF upto 240 sqmm XLPE cable | No. | 53784.99 |  |  | RATE EXCLUDING G.S.T.
7130352012 | 33 kV End terminating jointing kit TOUCH PROOF upto 300 sqmm XLPE cable | No. | 57370.66 |  |  | RATE EXCLUDING G.S.T.
7130352013 | 33 kV End terminating jointing kit TOUCH PROOF upto 400 sqmm XLPE cable | No. | 58685.4 |  |  | RATE EXCLUDING G.S.T.
7130352014 | LT End termination jointing kit for 4-core 300 sq.mm. XLPE underground cable | Set | 860.97 |  |  | RATE EXCLUDING G.S.T.
3.5 Core, 1.1 kV LT PVC Armoured Cable :-
7130311015 | 16 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 150 |  |  | RATE EXCLUDING G.S.T.
7130311016 | 25 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 191.86 |  |  | RATE EXCLUDING G.S.T.
7130311017 | 50 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 280.23 |  |  | RATE EXCLUDING G.S.T.
7130311018 | 70 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 367.43 |  |  | RATE EXCLUDING G.S.T.
7130311019 | 95 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 448.83 |  |  | RATE EXCLUDING G.S.T.
7130310093 | 120 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 553.48 |  |  | RATE EXCLUDING G.S.T.
7130311020 | 150 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 656.96 |  |  | RATE EXCLUDING G.S.T.
7130311021 | 185 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 808.12 |  |  | RATE EXCLUDING G.S.T.
7130311031 | 240 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1017.42 |  |  | RATE EXCLUDING G.S.T.
7130311032 | 300 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1236.02 |  |  | RATE EXCLUDING G.S.T.
7130310094 | 400 Sq.mm., 3.5 Core, 1.1 kV LT PVC Armoured Cable | Per Mtr. | 1558.11 |  |  | RATE EXCLUDING G.S.T.
7130870011 | Copper Bonded Ground Rod 25 mm, 3 Mtr long (For transformer body and neutral earthing) | No. | 14206.7463 |  |  | RATE EXCLUDING G.S.T.
7130870012 | Copper Bonded Ground Rod 17.2 mm, 3 Mtr long (For earthing of rest of the body) | No. | 11471.81 |  |  | RATE EXCLUDING G.S.T.
7132490002 | Chemical earthing Compound (1 packet of 25 kg) 2 packet per earth pit | Packet | 1353.38 |  |  | RATE EXCLUDING G.S.T.
7130870014 | Copper bonded strip 25x3 mm. (0.65 kg/Mtr) | Mtr. | 333.44 |  |  | RATE EXCLUDING G.S.T.
7132461002 | HDPE Pipe OD 250mm, PN10 PE100, SDR 13.6 made of virgin material | Mtr. | ITEM DELETED |  |  | ITEM DELETED NOT TO BE USED
11/0.4 kV Compact Sub-station
7131941008 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 1600 Amp. +Transformer of 1000 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 6 nos., MCCB rating - 400 Amp. | No. | 4368664.87 |  |  | RATE EXCLUDING G.S.T.
7131941009 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 800 Amp. +Transformer of 500 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 4 nos., MCCB rating - 400 Amp. | No. | 3320749.03 |  |  | RATE EXCLUDING G.S.T.
7131941010 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 630 Amp. +Transformer of 315 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 4 nos., MCCB rating - 200 Amp. | No. | 2701840.91 |  |  | RATE EXCLUDING G.S.T.
7131941011 | Compact arrangement of 3 Way RMU consist of 2 LBS+1VCB (without FRTU)+LT indoor Panel with Aluminium bus bar fixed with ACB rating 400 Amp. +Transformer of 200 kVA, 11/0.4 kV, Copper Wound Cast ONAN, losses as per latest amendment of IS :1180, LT Outgoing - 2 nos., MCCB rating - 200 Amp. | No. | 2385698.53 |  |  | RATE EXCLUDING G.S.T.
7130310091 | XLPE insulated PVC sheathed 4 core 300 Sq.mm. Armoured LT underground cable | Mtr. | 1239.51 |  |  | RATE EXCLUDING G.S.T.
7131960012 | Indoor, floor mounted 33 KV Transformer control switchboard comprising of 1 vertical panels which horizontal top bus bars of Al, rated for 800 A VCBs , in draw out executions. The VCB shall be rated for 36KV, 1600 A, 26kA. The panels shall be complete with all accessories, hardwares, heater etc. as required for completeness. Panel for controlling 5MVA power transformer with VCB, CTs, PTs,digital meters, Trivector Energy Meters, transformer protection relays, auxiliary relays etc. | Each | 1721033.26 |  |  | RATE EXCLUDING G.S.T.
7131960013 | Indoor, floor mounted 33KV feeder control switchboard comprising of 1 vertical panels which horizontal top bus bars of Al, rated for 800 A VCBs , in draw out executions. The VCB shall be rated for 36KV, 1600 A, 26kA. The panels shall be complete with all accessories, hardwares, heater etc. as required for completeness. Panel for controlling outgoing/ Bus coupler with VCB, CTs, digital Ammeter/voltmeter/ Trivector Energy meter, O/C and E/F relay etc. The cable chamber shall have 3 nos., 20kV, 10 kA distribution class valve type lightning arresters. | Each | 1721033.26 |  |  | RATE EXCLUDING G.S.T.
7131960014 | Indoor, floor mounted 11KV Transformer control switchboard of 01vertical panel with horizontal top bus bars of Al rated for 800 A, VCBs and LBS, in draw out executions. The VCB shall be rated for 12KV, 18.4kA. The panels shall be complete with all accessories, hard wares, heater etc. as required for completeness. Panel for controlling incomer with VCB of 800 A ratings, CTs, PTs, digital Ammeter/ voltmeter/ Trivector Energy meter, O/C and E/F relay etc. | Each | 1182257.4025 |  |  | RATE EXCLUDING G.S.T.
7131960015 | Indoor, floor mounted 11KV feeder control switchboard of 01vertical panel with horizontal top bus bars of Al rated for 800 A, VCBs and LBS, in draw out executions. The VCB shall be rated for 12KV, 18.4kA. The panels shall be complete with all accessories, hard wares, heater etc. as required for completeness. Panel for controlling outgoing feeders with VCB of 400A rating, CTs, digital meter, Trivector Energy Meters, O/C and E/F relay, auxiliary relays etc. | Each | 1182257.4 |  |  | RATE EXCLUDING G.S.T.
7132230001 | 11 kV Current Transformer Resin type, Ratio 200-100/5 Indoor Type | Each | 67006.48 |  |  | RATE EXCLUDING G.S.T.
7132230003 | 11 kV Current Transformer Resin type, Ratio 300-150/5 Indoor Type | Each | 55527.95 |  |  | RATE EXCLUDING G.S.T.
7132230004 | 11KV Potential Transformer Resin type, [Indoor Type] | Each | 125922.46 |  |  | RATE EXCLUDING G.S.T.
7130641035 | G.l. Pipe 150 mm OD (Class B as per railway) | Per Mtr | 1487.06 | G.I. Pipe 150mm
7132461804 | HDPE pipe of size 160 mm OD/140 mm ID PN 10 PE 100 HDR | Per Mtr | 1294.34 | HDPE pipe size 160mm OD/140mm ID PN10
7131950210 | SMC LT Distribution Box for 200 kVA Distribution Transformer | Each | 22892.01 | SMC LT Distribution Box for 200 KVA Xmer
7131382840 | Microprocessor based single phase fully automatic oil BDV Test Kit | No | 250750 | Transformer oil BDV test kit |  | New item introduced
7131300014 | Digital weighing Machine (Range 50 g to 500 kg) | No | 20532 | Digital weighing machine |  | New item introduced
7131300015 | Digital vernier calipers(0-200 mm Range,Accuracy 0.01 mm) | No | 3315.8 | Digital vernier calipers |  | New item introduced
7131300016 | Digital Screw Gauge (0-25 mm Range,Accuracy 0.01 mm) | No | 4576.04 | Digital screw gauge |  | New item introduced
7131300017 | Measuring Tape (30 meter length) | No | 290.28 | Measuring tape |  | New item introduced
7131300018 | Laser Gun( Measure distance upto 125 meter and should be operational during day time also) | No | 20414 | Laser gun |  | New item introduced
7131960101 | MCR panel for 33 KV O/D VCB Feeder protection | EA | 205202 | MCR Panel for 33 KV O/D VCB Feeder Prot. |  | New item introduced
7131960102 | MCR panel for feeder & Capacitor Bank protection 11 KV | EA | 205202 | MCR Panel for Feeder & CapBank Prot 11KV |  | New item introduced
7131960103 | MCR panel for LV | EA | 211574 | MCR Penal for LV |  | New item introduced
7131961532 | RTU base equipment comprising panels,racks, sub-racks, CPU, interfacing equipment, required converters & all other required items/accessories including complete wiring for all modules(with WAN router MPLS connection port & with dual SIM ports and HMI of Min 10 '' Size) | EA | 430700 | Penal Pre wired RTU Integr. with BCPU |  | New item introduced
7130310101 | LAN cable armoured CAT6 (SFTP) | Mtr | 159.3 | LAN Cable Armoured CAT 6 (SFTP) |  | New item introduced
7130640033 | GI Conduit flexible with PVC coating | Mtr | 88.5 | GI Conduit flexible with PVC coating |  | New item introduced
7132468020 | 24 V DCPS with 8 Hrs back up (24 V DCPS to be provided for RTU and MCRP solutions with 3 years battery warranty) | EA | 142190 | 24V DCPS with 8 Hrs Backup |  | New item introduced
7130310105 | Cable 1.1 Kv 4C x 4 Sqmm Cu Unarmoured PVC | Mtr | 312.7 | Cable 1.1KV 4Cx4 Sqmm Cu Unarmoured PVC |  | New item introduced
7130310106 | Control cable 1.1 KV Cu 4C x 2.5 Sqmm Armoured | Mtr | 247.8 | Control Cable 1.1KV Cu 4Cx2.5 Sqmm Armrd |  | New item introduced
7130310109 | Control cable 1.1 KV Cu 10C x 1.5 Sqmm Armoured PVC | Mtr | 348.1 | Control Cable 1.1KV Cu 10Cx1.5 Sqmm Arm. |  | New item introduced
| 11 KV DO Fuse Element:- |  |  |  |  | New item introduced
7131900501 | 1.5 Amp | No | 25.96 | FUSE ELEMENT 1.5 AMPS FOR 11 KV D O |  | New item introduced
7131900504 | 3 Amp | No | 27.14 | FUSE ELEMENT 3 AMPS FOR 11 KV D O |  | New item introduced
7131900505 | 5 Amp | No | 28.32 | FUSE ELEMENT 5 AMPS FOR 11 KV D O |  | New item introduced
7131900525 | 25 Amp | No | 25.96 | FUSE ELEMENT 25 AMPS FOR 11 KV D O |  | New item introduced
7130310108 | Single core XLPE insulated, PVC sheathed unarmoured cable : - 400 Sqmm | Km. | 431043.65 | 1CX 400 SQMM(AL) XLPE, PVC SHEATED UNARM |  | New item introduced
7132504016 | 32 Volts 100 AH Lithium Ferro Battery | No. | 96760 | 32V 100AH Lithium ferro phosphate battry |  | New item introduced
7131961530 | Modem(NBIoT) | Nos. | 5780.82 | NBIoT Modems |  | New item introduced
7130530610 | CT/PT Unit Scrap 33 KV | No. | 17702.09 | PT SCRAP 33 KV |  | New item introduced
Note on B154: Author: old name I-Bolt (big size)
Note on D190: Author: GST applicable separately.
Note on D191: Author: GST applicable separately.
Note on D381: Author: GST applicable separately.
Note on D399: Author: GST applicable separately.
Note on D409: Author: GST applicable separately.
Note on A432: Author: bin code changed old bin no was 7131900875
Note on D598: Author: GST applicable separately.
Note on D599: Author: GST applicable separately.
Note on D614: Author: GST applicable separately.
Note on D615: Author: GST applicable separately.
Note on D616: Author: GST applicable separately.
Note on D620: Author: GST applicable separately.
Note on D622: Author: GST applicable separately.
Note on D732: Author: GST applicable separately.
Note on D736: Author: GST applicable separately.
Note on D791: Author: GST applicable separately.
Note on D793: Author: GST applicable separately.
Note on D794: Author: GST applicable separately.
Note on D795: Author: GST applicable separately.
Note on D796: Author: GST applicable separately.
Note on D797: Author: GST applicable separately.
Note on D798: Author: GST applicable separately.
Note on D800: Author: GST applicable separately.
Note on D801: Author: GST applicable separately.
Note on D803: Author: GST applicable separately.
Note on D804: Author: GST applicable separately.
Note on D805: Author: GST applicable separately.
Note on D806: Author: GST applicable separately.
Note on D807: Author: GST applicable separately.
Note on D808: Author: GST applicable separately.
Note on D809: Author: GST applicable separately.
Note on D810: Author: GST applicable separately.
Note on D811: Author: GST applicable separately.
Note on D813: Author: GST applicable separately.
Note on D814: Author: GST applicable separately.
Note on D815: Author: GST applicable separately.
Note on D816: Author: GST applicable separately.
Note on D817: Author: GST applicable separately.
Note on D819: Author: GST applicable separately.
Note on D820: Author: GST applicable separately.
Note on D821: Author: GST applicable separately.
Note on D823: Author: GST applicable separately.
Note on D824: Author: GST applicable separately.
Note on D825: Author: GST applicable separately.
Note on D826: Author: GST applicable separately.
Note on D827: Author: GST applicable separately.
Note on D828: Author: GST applicable separately.
Note on D829: Author: GST applicable separately.
Note on D830: Author: GST applicable separately.
Note on D831: Author: GST applicable separately.
Note on D832: Author: GST applicable separately.
Note on D833: Author: GST applicable separately.
Note on D834: Author: GST applicable separately.
Note on D835: Author: GST applicable separately.
Note on D836: Author: GST applicable separately.
Note on D837: Author: GST applicable separately.
Note on D838: Author: GST applicable separately.
Note on D840: Author: GST applicable separately.
Note on D841: Author: GST applicable separately.
Note on D842: Author: GST applicable separately.
Note on D843: Author: GST applicable separately.
Note on D845: Author: GST applicable separately.
Note on D846: Author: GST applicable separately.
Note on D847: Author: GST applicable separately.
Note on D848: Author: GST applicable separately.
Note on D850: Author: GST applicable separately.
Note on D851: Author: GST applicable separately.
Note on D852: Author: GST applicable separately.
Note on D853: Author: GST applicable separately.
Note on D854: Author: GST applicable separately.
Note on D855: Author: GST applicable separately.
Note on D856: Author: GST applicable separately.
Note on D857: Author: GST applicable separately.
Note on D858: Author: GST applicable separately.
Note on D859: Author: GST applicable separately.
Note on D860: Author: GST applicable separately.
Note on D861: Author: GST applicable separately.
Note on D862: Author: GST applicable separately.
Note on D863: Author: GST applicable separately.
Note on D864: Author: GST applicable separately.
Note on D867: Author: GST applicable separately.
Note on D868: Author: GST applicable separately.
Note on D869: Author: GST applicable separately.
Note on D870: Author: GST applicable separately.
Note on D871: Author: GST applicable separately.
Note on D872: Author: GST applicable separately.
Note on D873: Author: GST applicable separately.
Note on D874: Author: GST applicable separately.
Note on D875: Author: GST applicable separately.
Note on D876: Author: GST applicable separately.
Note on D877: Author: GST applicable separately.
Note on D878: Author: GST applicable separately.

## B-1
COST SCHEDULE B -1
2026-27
SCHEDULE FOR 33/11 kV, 3.15 MVA, 1.6 MVA SUB-STATION WITH TWO BAYS FOR OUTGOING FEEDERS AND 5 MVA SUB-STATION WITH THREE BAYS FOR OUTGOING FEEDERS AT NEW SITE
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Proposed 33/11 kV S/s expandable to 2x1.6 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x3.15 MVA with control room |  | Proposed 33/11 kV S/s expandable to 2x5 MVA with control room
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 |  | LAND AND CIVIL WORKS (Rate as per SoR PWD)
| i(a) | Const. of 2.10 M high brick masonry boundary wall on hard soil/hard moorum (Non-Expansive Soil). (As per Drg. No. 04-01/ST-29/R2) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 3597 | 400 | 1438800 | 400 | 1438800 | 400 | 1438800 | (NAME CHANGED)Please select any one appropriate row out of three at S.No. 1 [ { i (a) }, { i (b) } or { i (c) } ] according to actual field condition as per type of soil strata.
| i(b) | Const. of 2.10 M high brick masonry boundary wall on Black Cotton Soil (Expansive Soil). (As per Drg. No. 04-04/ST-29/R2 and ST/750) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 3765 | 400 | 1506000 | 400 | 1506000 | 400 | 1506000 | NAME CHANGED
| i(c) | Const. of 2.40 M high brick masonry boundary wall iec concerntina coil fencing (As per Drg. No. 04-01/ST-103 date 15.01.2010) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 6248 | 400 | 2499200 | 400 | 2499200 | 400 | 2499200 | NEW ROW ADDED(select where ground level is down and additional security is required)
| ii | Drilling of 150 mm dia bore well (upto 100 M depth) with G.I. Casing upto 30 M depth or as per requirments, 1.5 HP Submersible motor pump, 32 mm dia. HDPE roll pipe PE-80 (appr. 90 M depth or as per requirments), 3x2.5 Sq.mm. submersible cable, rope wire and CPVC pipes for water supply line for switch yard (appr. 20 mm OD 30 M long & 32 mm OD 150 M long) i/c T&P, materials, labours, transportation etc complete. |  | Job | 158773 | 1 | 158773 | 1 | 158773 | 1 | 158773
| iii | CONTROL ROOM
| (A) | Urban Type Control Room
| A(i) | Construction of Urban Type Control Room (Previously known as A-1 Type Control Room) with toilet as per Drg. No. 04-01/AR/24-R2 date 13.06.2007 i/c royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 924325 | 1 | 924325 | 1 | 924325 | 1 | 924325
| A(ii) | Extra for Additional height of DPC level for every 0.30 M height or part thereof over 1.20 M height for Urban Type Control Room. |  | Job | 21008 | 1 | 21008 | 1 | 21008 | 1 | 21008
| (B) | Rural Type Control Room
| B(i) | Construction of Rural Type Control Room building (on Hard Soil) with toilet & store room as per Drg. No. 04-03/Civil-Distt/23-24/CR(R)/H.S./01 to 09 dt 10.01.2024 i/c royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 850478 | 1 | 850478 | 1 | 850478 | 1 | 850478
| B(ii) | Construction of Rural Type Control Room building (on Black Cotton Soil) with toilet & store room as per Drg. No. 04-03/Civil-Distt/23-24/CR(R)/B.C.S./01 to 10 dt 10.01.2024 i/c royalty, T&P, materials, labours, transportation etc. complete. |  | Job | 934948 | 1 | 934948 | 1 | 934948 | 1 | 934948 | (Please select any one appropriate row out of two at S.No.1[ B(i) or B(ii)] according to actual field condition as per type of soil strata.)
| B(iii) | Extra for Additional height of DPC level for every 0.30 M height or part thereof over 1.20 M height for Rural Type of Control Room. |  | Job | 16050 | 1 | 16050 | 1 | 16050 | 1 | 16050
| iv (a) | Construction of 2.40 M high chain link wire mesh fencing on Hard Soil or Hard Moorum (Non Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | M | 2756 | 125 | 344500 | 125 | 344500 | 125 | 344500
| iv (b) | Construction of 2.40 M high chain link wire mesh fencing on Black Cotton Soil (Expansive Soil), as per Drg. No. 04-01/ST/62R, including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | M | 3176 | 125 | 397000 | 125 | 397000 | 125 | 397000 | Please select any one appropriate row out of two at S.No. 1 [ { iv (a) } or { iv (b) } ] according to actual field condition as per type of soil strata.
| v | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | Each | 36900 | 2 | 73800 | 2 | 73800 | 2 | 73800
| vi | Providing and filling in plinth with sand / crusher dust and hard moorum under floor in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering with a lead upto 50 M and lift upto 1.5 M. (Moorum measured in stacks will be reduced by 16% for voids). |  | CUM | 371 | 300 | 111300 | 300 | 111300 | 300 | 111300
| vii | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | CUM | 1200 | 180 | 216000 | 180 | 216000 | 180 | 216000
| viii (a) | Construction of 3.75 M wide C.C. road on hard soil or hard moorum (Non Expansive Soil), as per Drg. No. 04-01/CON/44 including cost of mixture machine, vibrator, curing, all materials, T&P, labour, transportation, loading, unloading, royalty etc. complete. |  | Mtr | 3464 | 120 | 415680 | 120 | 415680 | 120 | 415680
| viii (b) | Construction of 3.75 M wide C.C. road on black cotton soil (Expansive Soil), as per Drg. No. 04-01/CON/44, including cost of mixture machine, vibrator, curing, all materials, T&P, labour, transportation, loading, unloading, royalty etc. complete. |  | Mtr | 4124 | 120 | 494880 | 120 | 494880 | 120 | 494880 | Please select any one appropriate row out of two at S.No. 1 [ { viii (a) } or { viii (b) } ] according to actual field condition as per type of soil strata.
| ix | Construction of 7.50 M long 600 mm internal dia. NP-3 Hume pipe culvert as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | No. | 33635 | 1 | 33635 | 1 | 33635 | 1 | 33635
| x (a) | Construction of 1.0 M high (from G.L.) brick masonary retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 2912 | 130 | 378560 | 130 | 378560 | 130 | 378560 | Please select any one appropriate row out of nine at S.No. 1 [ { x (a) }, {x (b)}, {x (c)}, {x (d)}, {x (e)} ,{x (f)},{x (g)},{x (h)} or { x (i) } ] according to actual field condition as per type of soil strata.
| x (b) | Const. of 1.0 M high (From G.L.) Stone masonry retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 3876 | 130 | 503880 | 130 | 503880 | 130 | 503880
| x (c) | Const. of 1.5 M high (From G.L.) Stone masonry retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 5788 | 130 | 752440 | 130 | 752440 | 130 | 752440
| x (d) | Const. of 2.0 M high (From G.L.) Stone masonry retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 7492 | 130 | 973960 | 130 | 973960 | 130 | 973960
| x (e) | Const. of 2.5 M high (From G.L.) Stone masonry retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 9793 | 130 | 1273090 | 130 | 1273090 | 130 | 1273090
| x (f) | Const. of 3.0 M high (From G.L.) Stone masonry retaining wall as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 12458 | 130 | 1619540 | 130 | 1619540 | 130 | 1619540
| x (g) | Const. of R.C.C retaining wall,1.0 M high (From G.L.) as per drawing Nos.04-01/ST/220 date 10.08.2016 including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 7014 | 130 | 911820 | 130 | 911820 | 130 | 911820 | NEW ROW ADDED(Select where availibility of stone is less)
| x (h) | Const. of R.C.C retaining wall,2.0 M high (From G.L.) as per drawing Nos.04-01/ST/220 date 10.08.2016 including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 15087 | 130 | 1961310 | 130 | 1961310 | 130 | 1961310 | NEW ROW ADDED(Select where availibility of stone is less)
| x (i) | Const. of R.C.C retaining wall,3.0 M high (From G.L.) as per drawing Nos.04-01/ST/220 date 10.08.2016 including all labour, T&P, curing, materials, transportation, loading, unloading, royalty etc. complete. |  | RM | 24494 | 130 | 3184220 | 130 | 3184220 | 130 | 3184220 | NEW ROW ADDED(Select where availibility of stone is less)
| xi | Providing filling and compacting local earth (from approved source pit) in layers not exceeding 20 cm in depth consolidating each deposited layer by ramming and watering, including dressing etc. complete(Local earth measured in stacks will be reduced by 20 % for voids) |  | Cu. M | 242 | 600 | 145200 | 600 | 145200 | 600 | 145200
| xii | Const. of Brick masonary cable trench (Inside size 300 mm x 300 mm), with 200 mm thick walls and MS flat 40x5 mm @ 0.60 M c/c with standard drawings, i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 2155 | 80 | 172400 | 80 | 172400 | 80 | 172400
| xiii | Sub total-1 | 7: 4433981; 9: 4433981; 11: 4433981 | Please select any one appropriate row [A] out of three for S.No. 1 [ { i (a) }, { i (b) } or { i (c) } ;;[B] out of two for S.No. 1[ {iii(A) or iii(B)} ] ;; [C] out of two for S.No.1 [ B(i) or B(ii)] ;; [D] out of two for S.No. 1 [{ iv (a) } or { iv (b) } ;; [E] out of two for S.No. 1 [ { viii (a) } or { viii (b) } ;; & [F] out of nine for S.No. 1 [ { x (a) }, { x (b)}, { x (c)}, { x (d)}, { x (e)} , { x (f)}, { x (g)}, { x (h)}or { x (i) }] according to actual field condition as per type of soil strata.
2 |  | EQUIPMENTS
| i | 33/11 kV transformer 1.60 MVA | 7132220091 | No | 1500128.26 | 1 | 1500128.26 | -- | -- | -- | --
|  | 33/11 kV transformer 3.15 MVA | 7132220095 | No | 4456033.02 | -- |  | 1 | 4456033.02 | -- | --
|  | 33/11 kV transformer 5.00 MVA | 7132220097 | No | 6078909.05 | -- |  | -- |  | 1 | 6078909.05
| ii | 33 kV VCB (With CT's & panel) | 4: No; 5: 399261.36; 6: --; 8: 1
|  | (i) 33 kV VCB (Without CT's & Panel) | 7131943380 | No | 280899.21 | 1 | 280899.21 | 1 | 280899.21 | 1 | 280899.21
|  | (ii) 33 kV Control Panel | 7131960524 | No | 43018.74 | 1 | 43018.74 | 1 | 43018.74 | 1 | 43018.74
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 25114.47 | 3 | 75343.41 | 3 | 75343.41 | 3 | 75343.41
| iii | 11 kV VCB for X'mer protection (With CTs & panel) | 4: No; 5: 242122.12; 6: 1; 8: 1; 10: 1
|  | (i) 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 154192.41 | 1 | 154192.41 | 1 | 154192.41 | 1 | 154192.41
|  | (ii) 11 kV Control Panel for Transformer Protection | 7131960522 | Each | 42392.8 | 1 | 42392.8 | 1 | 42392.8 | 1 | 42392.8
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | No | 15178.97 | 3 | 45536.91 | 3 | 45536.91 | 3 | 45536.91
| iv | 11 kV VCB for feeder protection with CTs & panel. | 4: No; 5: 473560; 6: 2; 8: 2; 10: 3
|  | (i) 11 kV VCB with Relay & Control Panel | 7131960497 | No | 182317.1 | 2 | 364634.2 | 2 | 364634.2 | 3 | 546951.3 | 7131941762+7131960008=7131960497(154192.41+28124.69=182317.1)
|  | (ii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 18154.3 | 6 | 108925.8 | 6 | 108925.8 | 9 | 163388.7
| v | 33 kV Isolator (600 A.) Set without earth switch | 7131930752 | No | 45159.49 | 2 | 90318.98 | 2 | 90318.98 | 2 | 90318.98
| vi | 11 kV Isolator (600 A.) (including 2 Nos. for capacitor bank) Set | 7131930663 | No | 26094.57 | 6 | 156567.42 | 6 | 156567.42 | 8 | 208756.56
| vii | 33 kV DO Fuse unit | 7131930415 | Each | 3310.46 | 3 | 9931.38 | 3 | 9931.38 | 9 | 29794.14
| viii | 11 kV DO Fuse unit | 7131930412 | Each | 1237.27 | 3 | 3711.81 | 3 | 3711.81 | 6 | 7423.62
| ix | 33 kV Porcelain Lightning Arrestors | 7130840021 | Each | 4289.09 | 3 | 12867.27 | 3 | 12867.27 | 3 | 12867.27
| x | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 327.8 | 12 | 3933.6 | 12 | 3933.6 | 15 | 4917
| xi | 33 kV Porcelain AB Switch | 7131930321 | Each | 23249.28 | 1 | 23249.28 | 1 | 23249.28 | 1 | 23249.28
| xii | 11 kV Porcelain AB Switch | 7131930221 | Each | 10471.34 | 3 | 31414.02 | 3 | 31414.02 | 4 | 41885.36
| xiii | Single phase 33 kV PT | 7132230057 | Each | 22774.85 | 3 | 68324.55 | 3 | 68324.55 | 3 | 68324.55
| xiv | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 103432.83 | 1 | 103432.83 | 1 | 103432.83 | 1 | 103432.83
| xv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 46601.35 | 2 | 93202.7 | 2 | 93202.7 | 3 | 139804.05
| xvi | Single phase 11 kV PT's | 7132230056 | Each | 14164.44 | 3 | 42493.32 | 3 | 42493.32 | 3 | 42493.32
| xvii | LT Meter (CT Operated) 100/5 A with CT's | 4: No; 5: 4185.2; 6: 1; 8: 1; 10: 1
|  | (i) CT operated electronic static bidirectional meters with DLMS Protocol. | 7131310997 | No | 2075.36 | 1 | 2075.36 | 1 | 2075.36 | 1 | 2075.36
|  | (ii) LT CT 100/5 A | 7132230016 | No | 527.46 | 4 | 2109.84 | 4 | 2109.84 | 4 | 2109.84
| xviii | H.T. STATIC TRIVECTOR METERS | 4: No; 5: 14361.45; 6: 3; 8: 3; 10: 4
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4787.15 | 3 | 14361.45 | 3 | 14361.45 | 4 | 19148.6
| xix | Lead Acid Battery with automatic charger | 4: No; 5: 85487.02; 6: 1; 8: 1; 10: 1
|  | (i) Battery | 7132404366 | No | 67787.02 | 1 | 67787.02 | 1 | 67787.02 | 1 | 67787.02
|  | (ii) Battery Charger | 7132468558 | No | 17700 | 1 | 17700 | 1 | 17700 | 1 | 17700
| xx | 33/0.4 kV station transformer (50 kVA) | 7132210215 | Each | 251830.58 | 0 | 0 | 0 | 0 | 2 | 503661.16
| xxi | Energy efficiency Level-1, 11/0.4 kV station transformer (100 kVA) [Without Box] * | 7132210020 | Each | 164821.1 | 1 | 164821.1 | 1 | 164821.1
| xxii | LT Distribution box for 63 kVA X'mer | 7131950065 | Each | 18891.13 | 0 | 0 | 0 | 0 | 2 | 37782.26
| xxiii | LT Distribution box for 100 kVA X'mer | 7131950105 | Each | 23614.9 | 1 | 23614.9 | 1 | 23614.9
| xxiv | Transformer clamping with 50x50x6 mm angle with 2 cross fixing channel | 7130600023 | Kg | 45.5205 | 20 | 910.4092 | 20 | 910.4092 | 20 | 910.4092
| xxv | Transformer & Distribution Box belting with 50x50x6 mm angle with 2 cross fixing channel | 7130600023 | Kg | 45.5205 | 108 | 4916.2097 | 108 | 4916.2097 | 108 | 4916.2097
| xxvi | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 6 Nos = 2448.6 Kgs | 7130601958 | Kg | 53.0776 | 2448.6 | 129965.7624 | 2448.6 | 129965.7624 | 2448.6 | 129965.7624
| xxvii | Control cable
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr. | 253.2528 | 360 | 91171.008 | 360 | 91171.008 | 480 | 121561.344
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr. | 132.305 | 360 | 47629.8072 | 360 | 47629.8072 | 510 | 67475.5602
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr. | 72.3623 | 180 | 13025.2194 | 240 | 17366.9592 | 300 | 21708.699
| xxviii | Tee Clamp for Dog Conductor | 7130830585 | No | 380.53 | 96 | 36530.88 | 96 | 36530.88 | 108 | 41097.24
| xxix | Danger Board for 33 kV & 11 kV equipment / supply pole | 7130880041 | No | 101.61 | 10 | 1016.1 | 10 | 1016.1 | 10 | 1016.1
| xxx | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 70.349 | 300 | 21104.706 | 300 | 21104.706 | 300 | 21104.706
| xxxi | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 4080.55 | 5 | 20402.75 | 5 | 20402.75 | 6 | 24483.3
| xxxii | Sub-total - 2 | 7: 3913661.4219; 9: 6873907.9217; 11: 9288403.0605
3 |  | STRUCTURE AND BUS BAR ARRANGEMENTS: -
| i | 8 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x8 mtr =296.8 kg/pole x 10 Nos = 2968 Kgs. | 7130601958 | Kg | 53.0776 | 2968 | 157534.2574 | 2968 | 157534.2574 | 3561.6 | 189041.1089
| ii | 7 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x7mtr = 259.7 Kg/pole x 4 Nos = 1038.8 Kgs. | 7130601958 | Kg | 53.0776 | 1038.8 | 55136.9901 | 1038.8 | 55136.9901 | 1038.8 | 55136.9901
| iii | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1x11 mtr =408.1 Kg/pole x 8 Nos = 3264.8 Kgs | 7130601958 | Kg | 53.0776 | 3264.8 | 173287.6832 | 3264.8 | 173287.6832 | 4081 | 216609.604
| iv | MS DC Cross arm (100 x 50 x 6 mm Channel) 5.2 Mtr long Set | 7130810684 | No | 9299.67 | 22 | 204592.74 | 22 | 204592.74 | 28 | 260390.76
| v | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | Set | 7486.37 | 2 | 14972.74 | 2 | 14972.74 | 9 | 67377.33
| vi | MS DC Cross arm (100 x 50 x 6 mm Channel) 2.7 Mtr long Set | 7130810608 | Set | 5912.78 | 10 | 59127.8 | 10 | 59127.8 | 12 | 70953.36
| vii | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1826.51 | 1 | 1826.51 | 1 | 1826.51 | 2 | 3653.02
| viii | R.S. Joist (175x85 mm) | 7130600675 | Kg | 56.7279 | 468 | 26548.6806 | 468 | 26548.6806 | 546 | 30973.4607
| ix | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 120.4014 | 500 | 60200.705 | 500 | 60200.705 | 600 | 72240.846
| x | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 378.54 | 15 | 5678.1 | 18 | 6813.72 | 21 | 7949.34
| xi | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 139.71 | 0 | 0 | 0 | 0 | 0 | 0
| xii | Polymer Disc Insulator for 33 kV Side | 7130820013 | Each | 187.29 | 81 | 15170.49 | 81 | 15170.49 | 99 | 18541.71
| xiii | 33 kV Strain Hardware fitting | 7130820248 | Each | 333.97 | 81 | 27051.57 | 81 | 27051.57 | 99 | 33063.03
| xiv | Polymer Disc insulator for 11 kV side (double disc) | 7130820010 | Each | 111.39 | 0 | 0 | 0 | 0 | 0 | 0
| xv | 33 kV Strain Plate 8 mm thick | 7130810624 | Each | 101.05 | 198 | 20007.9 | 198 | 20007.9 | 246 | 24858.3
| xvi | Clamp for H-Beam | 7130810692 | Pair | 362.75 | 64 | 23216 | 64 | 23216 | 66 | 23941.5
| xvii | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 40 | 7334.8 | 40 | 7334.8 | 45 | 8251.65
| xviii | Aluminium Paint | 7130210809 | Ltr | 409.72 | 40 | 16388.8 | 40 | 16388.8 | 45 | 18437.4
| xix | Sub-total - 3 | 7: 868075.7663; 9: 869211.3863; 11: 1101419.4097
4 |  | OTHER MISCELLANEOUS ITEMS: -
| i | Concreting of structures & foundation (1:3:6) | 7130200202 | Cmt | 2970 | 51.6 | 153252 | 60.6 | 179982 | 67.2 | 199584 | Material cost including GST and labour.
| ii | PVC insulated Single Core 70 Sqmm Armoured cable. | 7130311010 | Mtr. | 95.8181 | 10 | 958.181 | 10 | 958.181 | 10 | 958.181
| iii | 16 Sqmm 4-core Cable for Switch yard lighting, tripping arrangement & system control (armoured) | 7130311084 | Mtr. | 89.5467 | 300 | 26864.007 | 300 | 26864.007 | 300 | 26864.007
| iv | 18 W LED Street Light complete set | 7131210030 | Set | 2491.08 | 4 | 9964.32 | 4 | 9964.32 | 4 | 9964.32
| v | 70 W LED Street Light complete set | 7131210032 | Set | 4552.2 | 6 | 27313.2 | 6 | 27313.2 | 6 | 27313.2
| vi | AC Distribution board for AC/DC Supply | 7131920028 | No | 12330.35 | 1 | 12330.35 | 1 | 12330.35 | 1 | 12330.35
| vii | Fixing of 33/11 kV S/S (Name Plate) Board made up of 2 mm thick MS Sheet of size 5'x8' as per approved drawing. | 7132406800 | Job | 10253.32 | 1 | 10253.32 | 1 | 10253.32 | 1 | 10253.32
| viii | Earthing of Sub-station including Distribution Transformer earthing.
|  | (i)Copper Bonded Rod 25mm 3 Mtr long * | 7130870011 | No | 16763.9606 | 2 | 33527.9212 | 2 | 33527.9212 | 2 | 33527.9212
|  | (ii)Copper Bonded Rod 17.2mm, 3 Mtr long ** | 7130870012 | No | 13536.7358 | 10 | 135367.358 | 10 | 135367.358 | 12 | 162440.8296
|  | (iii)COMPOUND (1 packet of 25 kg) 2 packet per earth pit | 7132490002 | Packet | 1596.9884 | 22 | 35133.7448 | 22 | 35133.7448 | 24 | 38327.7216
|  | (iv)Copper bonded strip 25x3 mm (0.65kg/Mtr) | 7130870014 | Mtr. | 393.4592 | 200 | 78691.84 | 200 | 78691.84 | 200 | 78691.84
|  | (v)G.I.Nots & Bolts 16x40 mm | 7130620133 | kg | 120.28 | 1.5 | 180.42 | 1.5 | 180.42 | 1.5 | 180.42
|  | (vi)G.I.Nots & Bolts 16x55 mm | 7130620140 | kg | 120.28 | 1.5 | 180.42 | 1.5 | 180.42 | 1.5 | 180.42
|  | (vii)G.I. spring Washer | 7130622922 | kg | 152.82 | 1 | 152.82 | 1 | 152.82 | 1 | 152.82
|  | (viii)ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr. | 120.4014 | 150 | 18060.2115 | 150 | 18060.2115 | 150 | 18060.2115
|  | (ix)0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | 7130830055 | Mtr. | 36.1103 | 50 | 1805.514 | 50 | 1805.514 | 100 | 3611.028
|  | (x)Bimetallic Clamp | 7130830056 | No. | 616.6 | 16 | 9865.6 | 16 | 9865.6 | 16 | 9865.6
|  | (xi)Miscellaneous Items | 4: LS; 7: 1500; 9: 1500; 11: 1500
|  | (xii) MS flat 50x6 mm size (2.5 kg per meter) | 7130600173 | Kg | 51.0754 | 1000 | 51075.41 | 1000 | 51075.41 | 1000 | 51075.41
| ix | MS Nuts & Bolts | 4: Kg; 6: 186; 8: 270; 10: 270
|  | (i) MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 86.95 | 10 | 869.5 | 15 | 1304.25 | 15 | 1304.25
|  | (ii) MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 85.5 | 5 | 427.5 | 10 | 855 | 10 | 855
|  | (iii) MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 85.5 | 15 | 1282.5 | 25 | 2137.5 | 25 | 2137.5
|  | (iv) MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 84.05 | 66 | 5547.3 | 85 | 7144.25 | 85 | 7144.25
|  | (v) MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 84.05 | 80 | 6724 | 110 | 9245.5 | 110 | 9245.5
|  | (vi) MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 84.05 | 10 | 840.5 | 25 | 2101.25 | 25 | 2101.25
| ix | Furniture
|  | (i) Table 4'x2.5' | 7132476014 | No | 8968 | 1 | 8968 | 1 | 8968 | 1 | 8968
|  | (ii) Chair | 7132409830 | No | 4720 | 2 | 9440 | 2 | 9440 | 2 | 9440
|  | (iii)Small almirah 50", 20 SWG Sheet | 7132401672 | No | 8024 | 1 | 8024 | 1 | 8024 | 1 | 8024
| x | Fire fighting equipments
|  | (i) Fire fighting equipments (dry chemical powder type 5 Kg capacity) | 7132490006 | No | 5868.51 | 2 | 11737.02 | 2 | 11737.02 | 2 | 11737.02
|  | (ii) Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | 7132421002 | No | 6562.35 | 2 | 13124.7 | 2 | 13124.7 | 2 | 13124.7
| xi | Electrically insulated 11 kV mats infront of electrical control panel | 7132448003 | No | 6133.6 | 3 | 18400.8 | 3 | 18400.8 | 3 | 18400.8
| xii | Sub-total - 4 | 7: 691862.4575; 9: 725688.9075; 11: 777363.8699
5 |  | Total cost including Civil works { Sub total 1 without GST } and materials {( Sub total 2 + Sub total 3 + Sub total 4) including GST} | 7: 9907580.6457; 9: 12902789.2155; 11: 15601167.3401
6 |  | Total material cost including Civil works but excluding GST [2(xxxii)+3(xix)+4(xii) / 1.18)+1(xiii)] | 7: 9072624.7675; 9: 11610937.1148; 11: 13897698.2373
7 |  | Total material cost excluding Civil works and excluding GST [2(xxxii)+3(xix)+4(xii) / 1.18)] | 7: 4638643.7675; 9: 7176956.1148; 11: 9463717.2373
8 |  | Incidental Charges @ 7.5 % on " Serial No. - 7 " above (Serial No.- 7 * 0.075) | 5: 0.075; 7: 347898.2826; 9: 538271.7086; 11: 709778.7928
9 | (i) | Services on S/s earthing |  | No | 33626.88 | 1 | 33626.88 | 1 | 33626.88 | 1 | 33626.88
| (ii) | Services on Painting of structures |  | No | 21643.47 | 1 | 21643.47 | 1 | 21643.47 | 1 | 21643.47
| (iii) | Services on Labelling of equipments |  | No | 18036.23 | 1 | 18036.23 | 1 | 18036.23 | 1 | 18036.23
10 |  | Labour charges as per sch. (BL-1+BL-3+CL-23+CL-25) | 7: 319981.21; 9: 338214.17; 11: 382699.44
11 |  | Labour charges for concreting |  | Cmt | 740.31 | 51.6 | 38199.996 | 60.6 | 44862.786 | 67.2 | 49748.832
12 |  | LABOUR FOR DIGGING |  |  | 2572.5 | 4 | 10290 | 4 | 10290 | 4 | 10290
13 | A | Transportation of Power Transformer and Distribution Transformer of capacity 315 kVA & above
| (i) | Transportation charges upto 100 km @ 1% of the cost of 1.6 MVA, 3.15 MVA & 5 MVA Power Transformer | 5: 0.01; 7: 12712.9514; 9: 37762.9917; 11: 51516.1784
| B | Transportation of all other materials excluding Power Transformer and Distribution Transformer of capacity 315 kVA & above
| (i) | Transportation charges upto 100 km @ 2% of the cost of all other materials excluding (a) Civil Works; (b) DT 315 kVA and above capacity; & (c) PT of 1.6 MVA, 3.15 MVA & 5 MVA capacity | 5: 0.02; 7: 67346.9726; 9: 68013.1389; 11: 86241.988
14 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 6, 8, 9 [(i),(ii), (iii)], 10, 11,12,13[ {A(i)}, {B(i)} ] | 7: 1242795.095; 9: 1590207.3113; 11: 1907660.0061
15 |  | Total estimated cost of Sub-station (Including Civil works but excluding GST) [ Serial No. - 6, 8, 9 [(i),(ii), (iii)], 10, 11,12,13[ {A(i)}, {B(i)} ], 14 | 7: 11185155.8551; 9: 14311865.8013; 11: 17168940.0546
16 |  | Total Cost (Rs In lakhs) | 7: 111.8516; 9: 143.1187; 11: 171.6894
17 |  | Applicable CGST @ 9% on Serial No. - 15 | 5: 0.09; 7: 1006664.027; 9: 1288067.9221; 11: 1545204.6049
18 |  | Applicable SGST @ 9% on Serial No. - 15 | 5: 0.09; 7: 1006664.027; 9: 1288067.9221; 11: 1545204.6049
19 |  | Grand Total estimated cost of S/s including GST ( Serial No. - 15+17+18). | 7: 13198483.909; 9: 16888001.6455; 11: 20259349.2644
20 |  | Grand Total estimated cost including GST (Rounded off) | 7: 13198484; 9: 16888002; 11: 20259349
21 |  | Grand Total cost (Rs in LAKHS) | 7: 131.9848; 9: 168.88; 11: 202.5935
Note:
| (1) | All the rates are with considering price variation clause.
| (2) | Height of boundary wall for 33/11 Kv substation must be 7 Feet.
| (3) | In case of non-availability of H-Beam for structure double welded RS Joist may be used (1) 8 meter long double welded RS Joist and cost of it shall be taken in place of cost of item No.3 (i) & quantity should be 10 Nos for 3.15 & 1.6 MVA and 12 Nos for 5 MVA (2) 7 meter long double welded RS Joist and cost of it shall be taken as in place of cost of item No.3 (ii) & quantity should be 04 Nos each for 3.15 & 1.6 MVA and 5 MVA
| (4) | The cost of land is not taken in to account since normally CSPDCL acquires Govt. land at negligible cost. How ever needs to be procure other than Govt. land then should be added actual cost.
| (5) | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
| * | ISI Marked Energy Efficiency level-1 transformer
Note on C11: Smt. Prarthana Shukla: Earlier was-Const. of 1.50 M high brick masonry boundary wall on hard soil/hard moorum (Non-Expansive Soil). (As per Drg. No. 04-04/ST-60) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete.
Note on C12: Smt. Prarthana Shukla: Earlier was-Const. of 1.50 M high brick masonry boundary wall on Black Cotton Soil (Expansive Soil). (As per Drg. No. 04-04/ST-60) i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete.
Note on C21: Barun Chakraborty: Earlier name was - Construction of A1 type Control Room with toilet as per Drg. No. 04-01/AR/24-R2 date 13.06.2007 including all taxes royalty, T&P, materials, labours, transportation etc. complete.
Note on H42: 89326879: Please select any one appropriate row [A] out of three for S.No. 1 [ { i (a) }, { i (b) } or { i (c) } ;;[B] out of two for S.No. 1[ {iii(A) or iii(B)} ] ;; [C] out of two for S.No.1 [ B(i) or B(ii)] ;; [D] out of two for S.No. 1 [{ iv (a) } or { iv (b) } ;; [E] out of two for S.No. 1 [ { viii (a) } or { viii (b) } ;; & [F] out of six for S.No. 1 [ { x (a) }, { x (b)}, { x (c)}, { x (d)}, { x (e)} or { x (f) }] according to actual field condition as per type of soil strata.
Note on J42: Smt. Prarthana Shukla: Please select any one appropriate row [A] out of three for S.No. 1 [ { i (a) }, { i (b) } or { i (c) } ;;[B] out of two for S.No. 1[ {iii(A) or iii(B)} ] ;; [C] out of two for S.No.1 [ B(i) or B(ii)] ;; [D] out of two for S.No. 1 [{ iv (a) } or { iv (b) } ;; [E] out of two for S.No. 1 [ { viii (a) } or { viii (b) } ;; & [F] out of six for S.No. 1 [ { x (a) }, { x (b)}, { x (c)}, { x (d)}, { x (e)} or { x (f) }] according to actual field condition as per type of soil strata.
Note on L42: Smt. Prarthana Shukla: Please select any one appropriate row [A] out of three for S.No. 1 [ { i (a) }, { i (b) } or { i (c) } ;;[B] out of two for S.No. 1[ {iii(A) or iii(B)} ] ;; [C] out of two for S.No.1 [ B(i) or B(ii)] ;; [D] out of two for S.No. 1 [{ iv (a) } or { iv (b) } ;; [E] out of two for S.No. 1 [ { viii (a) } or { viii (b) } ;; & [F] out of six for S.No. 1 [ { x (a) }, { x (b)}, { x (c)}, { x (d)}, { x (e)} or { x (f) }] according to actual field condition as per type of soil strata.

## B-2
COST SCHEDULE B-2
2026-27
( 33 kV SUB-STATION )
POWER TRANSFORMERS
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | 1600 kVA | 3150 kVA | 5000 kVA
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Cost of Transformer as per Schedule of rates
| Power Transformer 1600 kVA | 7132220091 | No | 1500128.26 | 1 | 1500128.26
| Power Transformer 3150 kVA | 7132220095 | No | 4456033.02 | 1 |  | 4456033.02
| Power Transformer 5000 kVA | 7132220097 | No | 6078909.05 | 1 |  |  | 6078909.05
2 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 1500128.26 | 4456033.02 | 6078909.05
3 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 1271295.1356 | 3776299.1695 | 5151617.839
4 | Incidental Charges @ 7.5% on Serial No. - 3 |  |  | 0.075 |  | 95347.1352 | 283222.4377 | 386371.3379
5 | Labour charges as per Schedule BL-3 |  |  |  |  | 67962.73 | 82476.8 | 93294.69
6 | Transportation of Power Transformer
(i) | Transportation charges upto 100 km @ 1% of the cost of 1.6 MVA, 3.15 MVA & 5 MVA Power Transformer |  |  | 0.01 |  | 12712.9514 | 37762.9917 | 51516.1784
7 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 3, 4, 5, 6[(i)] |  |  |  |  | 180914.744 | 522470.1749 | 710350.0057
8 | Total Estimated Cost excluding GST ( Serial No. - 3, 4, 5, 6[(i)], 7) |  |  |  |  | 1628232.6961 | 4702231.5738 | 6393150.051
9 | Applicable CGST @ 9% on Serial No. - 8 |  |  | 0.09 |  | 146540.9427 | 423200.8416 | 575383.5046
10 | Applicable SGST @ 9% on Serial No. - 8 |  |  | 0.09 |  | 146540.9427 | 423200.8416 | 575383.5046
11 | Total Estimated Cost including GST (Row 8+9+10) |  |  |  |  | 1921314.5814 | 5548633.257 | 7543917.0601
12 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 1921315 | 5548633 | 7543917
Note:
(1) | All the rates are with considering price variation clause.
(2) | Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
Note on B20: Smt. Prarthana Shukla: Name Changed: Earlier was Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 2, 4, 5, 6

## B-3
COST SCHEDULE B-3
| ( 33 kV SUB-STATIONS ) | [6 empty] | 2026-27
SCHEDULE FOR INSTALLATION OF ADDITIONAL TRANSFORMER FOR PARALLEL OPERATION WITH TWO ADDITIONAL BAY ON 11 kV SIDE
S. No. | S.No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty | Sub-station capacity |  |  | Reason
[7 empty] | 1.6 MVA | 3.15 MVA | 5.0 MVA
1 | 2 |  | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 |  | EQUIPMENTS
| i | Power Transformer 33/11 kV
|  | Power Transformer 1.6 MVA | 7132220091 | No | 1500128.26 | 1 | 1500128.26
|  | Power Transformer 3.15 MVA | 7132220095 | No | 4456033.02 | 1 |  | 4456033.02
|  | Power Transformer 5 MVA | 7132220097 | No | 6078909.05 | 1 |  |  | 6078909.05
| ii | 33 kV VCB with CT's and panels. |  | No | 399261.36
|  | (i) 33 kV VCB ( without CT's and panels) | 7131943380 | No | 280899.21 | 1 |  | 280899.21 | 280899.21
|  | (ii) 33 kV Control Panel | 7131960524 | No | 43018.74 | 1 |  | 43018.74 | 43018.74
|  | (iii) 33 kV CT's (200-100/5-5) Amps | 7132230265 | No | 25114.47 | 3 |  | 75343.41 | 75343.41
| iii | 11 kV VCB for X'mer protection with CT's and panels. |  | No | 242122.12 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | Each | 154192.41 | 1 | 154192.41 | 154192.41 | 154192.41
|  | (ii) 11 kV Control Panel for X-mer Protection | 7131960522 | Each | 42392.8 | 1 | 42392.8 | 42392.8 | 42392.8
|  | (iii) 11 kV CT's 300-150/5 Amps | 7132230188 | Each | 15178.97 | 3 | 45536.91 | 45536.91 | 45536.91
| iv | 11 kV VCB for feeder protection with CT's and panels. |  | No | 473560 | 1
|  | (i) 11 kV VCB (without CTs & Panel) | 7131941762 | No | 154192.41 | 2 | 308384.82 | 308384.82 | 308384.82
|  | (ii) 11 kV Control Panel for feeder protection | 7131960008 | Each | 28124.69 | 2 | 56249.38 | 56249.38 | 56249.38
|  | (iii) 11 kV CT's 200-100/5 Amps | 7132230185 | No | 18154.3 | 6 | 108925.8 | 108925.8 | 108925.8
| v | 33 kV DO Fuse Unit | 7131930415 | Each | 3310.46 | 3 | 9931.38
| vi | 33 kV isolator, 600 A. Without earth switch | 7131930752 | No | 45159.49 | 2 | 90318.98 | 90318.98 | 90318.98
| vii | 11 kV isolator, 600 A | 7131930663 | No | 26094.57 | 5 | 130472.85 | 130472.85 | 130472.85
| viii | 33 kV Porcelain Lightning Arrestor | 7130840021 | Each | 4289.09 | 3 | 12867.27 | 12867.27 | 12867.27
| ix | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 327.8 | 9 | 2950.2 | 2950.2 | 2950.2
| x | H.T. STATIC TRIVECTOR METERS |  | No | 14361.45
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4787.15 | 3 | 14361.45 | 14361.45 | 14361.45
| xi | 33 kV Single Phase PT | 7132230057 | Each | 22774.85 | 3 | 68324.55 | 68324.55 | 68324.55
| xii | 11 kV Single Phase PT | 7132230056 | Each | 14164.44 | 3 | 42493.32 | 42493.32 | 42493.32
| xiii | 33 kV CTPT Unit 200-100/5 A | 7132230427 | Each | 103432.83 | 0 | 0 | 0 | 0
| xiv | 11 kV CTPT Unit 200-100/5 A | 7132230412 | Each | 46601.35 | 0 | 0 | 0 | 0
| xv | 33 kV Porcelain AB switch | 7131930321 | Each | 23249.28 | 0 | 0 | 0 | 0
| xvi | 11 kV Porcelain AB switch | 7131930221 | Each | 10471.34 | 2 | 20942.68 | 20942.68 | 20942.68
| xvii | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 4080.55 | 6 | 24483.3 | 24483.3 | 24483.3
| xviii | M.S.Angle 50*50*6 for Isolators clamping | 7130600023 | Kg | 45.5205 | 94.5 | 4301.6835 | 4301.6835 | 4301.6835
2 |  | STRUCTURE AND BUS BAR ARRANGEMENT
| (i) | D.O. Fuse supporting structure set on 7 Mtr long H- Beam 37.1 kg/mtr 33 kV & 11 kV side (2 No. each side) i.e. 37.1 kg x 7 = 259.7 kg/pole x 4 Nos = 1038.8 Kgs | 7130601958 | Kg | 53.0776 | 1038.8 | 55136.9901 | 55136.9901 | 55136.9901
| (ii) | 33 kV additional bay ( 02 No H-Beam 152x152 mm 08 mtr long) with 6 Nos, 5.2 Mtr channel |  | Set | 87304.8715 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 2 No = 593.60 Kgs | 7130601958 | Kg | 53.0776 | 593.6 | 31506.8515 | 31506.8515 | 31506.8515
|  | (ii) D.C.Cross arm Channel 5.2 mtr 100x50 mm | 7130810684 | No | 9299.67 | 6 | 55798.02 | 55798.02 | 55798.02
| (iii) | 11 kV, 2 Addl. bus bar structure 08 mtr long H- Beam 37.1 Kg/mtr with 4 Nos, 5.2 Mtr long DC cross arm (100 x 50 mm) |  | Set | 335162.1155 | 1
|  | (i) H-Beam 152x152 mm 08 mtr long 37.1 kg/mtr i.e.= 296.8 kg/pole x 4 No = 1187.2 Kgs. | 7130601958 | Kg | 53.0776 | 1187.2 | 63013.703 | 63013.703 | 63013.703
|  | (ii) H-Beam 152x152 mm 11 mtr long 37.1 kg/mtr i.e.= 408.1 kg/pole x 4 No = 1632.40 Kgs | 7130601958 | Kg | 53.0776 | 1632.4 | 86643.8416 | 86643.8416 | 86643.8416
|  | (iii) R.S. Joist (175x85 mm) [ 7x2.5 Mtr ] | 7130600675 | Kg | 56.7279 | 341 | 19344.231 | 19344.231 | 19344.231
|  | (iv) D.C.Cross arm Channel 5.2 mtr 100x50 mm (set) | 7130810684 | No | 9299.67 | 12 | 111596.04 | 111596.04 | 111596.04
|  | (v) D.C.Cross arm 5 ft. Centre 100x50 mm Channel | 7130810608 | Set | 5912.78 | 5 | 29563.9 | 29563.9 | 29563.9
|  | (vi) D.C.Cross arm 8 ft. Centre 100x50 mm Channel | 7130810517 | Set | 5000.08 | 5 | 25000.4 | 25000.4 | 25000.4
| (iv) | 60 Kg/Mtr 13.0 Mtr long Rails (60*5 = 300 Kg each) | 7130601072 | Kg | 70.349 | 300 | 21104.706 | 21104.706 | 21104.706
| (v) | ACSR Dog conductor | 7130830063 | Mtr | 120.4014 | 400 | 48160.564 | 48160.564 | 48160.564
| (vi) | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 378.54 | 3 | 1135.62 | 1135.62 | 1135.62
| (vii) | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | Each | 139.71 | 6 | 838.26 | 838.26 | 838.26
| (viii) | Strain hardware with strain set suitable for Dog conductor: -
|  | (a) 33 kV side with 3 disc insulator per phase. |  | Set | 37530.72 | 18
|  | (i) 33 kV Polymer Disc insulator . | 7130820013 | No | 187.29 | 72 | 13484.88 | 13484.88 | 13484.88
|  | (ii) 33 kV Strain Hardware | 7130820248 | Each | 333.97 | 72 | 24045.84 | 24045.84 | 24045.84
|  | (b) 11 kV side with 2 disc insulator per phase. |  | Set | 7275.6
|  | (i) 11 kV Polymer Disc insulator | 7130820010 | No | 111.39 | 0 | 0 | 0 | 0
|  | (ii) 11 kV Hardware | 7130820241 | No | 160.75 | 0 | 0 | 0 | 0
|  | (iii) Strain plate 8 mm thick | 7130810624 | No | 101.05 | 72 | 7275.6 | 7275.6 | 7275.6
| (ix) | T-clamp for jumper connection with AB Switches & DO fuses / Isolator. | 7130830585 | No | 380.53 | 96 | 36530.88 | 36530.88 | 36530.88
| (x) | Stay Clamp for "H" Beam | 7130810692 | Pair | 362.75 | 42 | 15235.5 | 15235.5 | 15235.5
| (xi) | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 6 | 1100.22 | 1100.22 | 1100.22
| (xii) | Aluminium Paint | 7130210809 | Ltr | 409.72 | 6 | 2458.32 | 2458.32 | 2458.32
3 |  | OTHER MISCELLANEOUS ITEMS
| i | Concreting of structure @ 0.45 Cmt. Per/pole bus structure (1:3:6) = 4.5 Cmt+0.65/pole*4+0.2*7 for isolator. | 7130200202 | Cmt | 2970 | 8.5 | 25245 | 25245 | 25245 | Material cost including GST and labour.
| ii | Concreting of Transformer foundation (1:3:6) = 15 cmt | 7130200202 | Kg | 2970 | 15 | 44550 | 44550 | 44550 | Material cost including GST and labour.
| iii | Concreting of 11 kV VCB foundation (1:3:6) = 18 cmt. | 7130200202 | Kg | 2970 | 18 | 53460 | 53460 | 53460 | Material cost including GST and labour.
| iv | Concreting of 33 kV VCB foundation (1:3:6) = 7 cmt. | 7130200202 | Kg | 2970 | 7 | 20790 | 20790 | 20790 | Material cost including GST and labour.
| v | Control cable for Xmer & VCB
|  | a) 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 253.2528 | 180 | 45585.504 | 45585.504 | 45585.504
|  | b) 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 132.305 | 720 | 95259.6144 | 95259.6144 | 95259.6144
|  | c) 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 72.3623 | 180 | 13025.2194 | 13025.2194 | 13025.2194
| vi | Earthing for addl X'mer & VCB
Document – As per W/o of G.S. Flat mesh earthing of 33/11 kV S/s as per No. CE/RR/TR/4328/9029 Raipur, Dt. 05/03/2007 (Rate taken from Sch.- III)
|  | (i) 25 mm dia 2500 mm. long G.I. rod earth electrodes | 7130642041 | No | 4423.96 | 9 | 39815.64 | 39815.64 | 39815.64
|  | (ii) GI Pipe of 40 mm dia 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 870.41 | 32 | 27853.12 | 27853.12 | 27853.12
|  | (iii) MS flat 50x6 mm size | 7130600173 | Kg | 51.0754 | 400 | 20430.164 | 20430.164 | 20430.164
|  | (iv) GI wire 8 SWG | 7130870043 | Kg | 69.8234 | 31 | 2164.5239 | 2164.5239 | 2164.5239
|  | (v) GI Nuts and bolts 16x40 mm | 7130620133 | Kg | 120.28 | 25 | 3007 | 3007 | 3007
|  | (vi) GI Nuts and bolts 16x65 mm | 7130620140 | Kg | 120.28 | 10 | 1202.8 | 1202.8 | 1202.8
|  | (vii) GI Spring washers | 7130622922 | Kg | 152.82 | 5 | 764.1 | 764.1 | 764.1
| vii | M.S. Nut- Bolts |  | Kg |  | 213
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 86.95 | 10 | 869.5 | 869.5 | 869.5
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 85.5 | 8 | 684 | 684 | 684
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 85.5 | 25 | 2137.5 | 2137.5 | 2137.5
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 84.05 | 70 | 5883.5 | 5883.5 | 5883.5
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 84.05 | 80 | 6724 | 6724 | 6724
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 84.05 | 20 | 1681 | 1681 | 1681
4 |  | SUB TOTAL - A (1+2+3) [Material cost including GST] |  |  |  |  | 3697364.5962 | 7042599.3362 | 8665475.3662
5 |  | Material cost excluding GST (Sub Total- A / 1.18) |  |  |  |  | 3133359.8273 | 5968304.5222 | 7343623.1917
6 |  | Incidental Charges @ 7.5% on Serial No. 5 :- |  |  | 0.075 |  | 235001.987 | 447622.8392 | 550771.7394
7 |  | (i) Services on Earthing |  | No. | 2484.99 | 8 | 19879.92 | 19879.92 | 19879.92
|  | (ii) Services on Painting |  | No. | 21643.47 | 1 | 21643.47 | 21643.47 | 21643.47
|  | Supply, stacking and spreading of 40 mm nominal size crusher broken hard stone (metal) i/c all labour, T&P, transportation, loading unloading, royalty etc. complete (Metal measured in stacks will be reduced by 8% for voids). |  | CUM | 1200 | 45 | 54000 | 54000 | 54000
|  | Services on Labelling of equipments |  | No | 18036.23 | 1 | 18036.23 | 18036.23 | 18036.23
|  | Services on X'mer foundation [2.5(L)*2(W)*3(H)] |  | Cmt | 5456.78 | 7.5 | 40925.85 | 40925.85 | 40925.85
|  | Services on foundation of 11 kV VCB [2(L)*2(W)*1.5(H)] |  | Cmt | 5456.78 | 9 | 49111.02 | 49111.02 | 49111.02
|  | Services on foundation of 33 kV VCB [2(L)*2(W)*1.75(H)] |  | Cmt | 5456.78 | 3.5 | 19098.73 | 19098.73 | 19098.73
|  | Construction of Brick masonary cable trench (inside size 300 mm x 300 mm.), with 200 mm. thick walls and MS Flat 40x5 mm @ 0.60 M c/c with standard drawings, i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 2155 | 45 | 96975 | 96975 | 96975
8 |  | Labour charges: - |  |  |  |  | 337594.215 | 352108.285 | 362926.175
| i | X'mer erection (Labour sch BL-3) |  |  |  |  | 67962.73 | 82476.8 | 93294.69
| ii | Other items as per schedule [Labour Schedule BL-2+(3*BL-4)+BL-6] |  |  |  |  | 233726.45 | 233726.45 | 233726.45
| iii | Labour charges for concreting |  | Cmt | 740.31 | 48.5 | 35905.035 | 35905.035 | 35905.035
9 | (A) | Transportation of Power Transformer
| i | Transportation charges upto 100 km @ 1% of the cost of 1.6 MVA, 3.15 MVA & 5 MVA Power Transformer |  |  | 0.01 |  | 12712.9514 | 37762.9917 | 51516.1784
| (B) | Transportation of all other materials excluding Power Transformer
| i | Transportation charges upto 100 km @ 2% of the cost of all other materials excluding (a) Civil Works; (b) PT of 1.6 MVA, 3.15 MVA & 5 MVA capacity |  |  | 0.02 |  | 37241.2938 | 43840.1071 | 43840.1071
10 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 5, 6, 7, 8, 9[ {A(i)}, {B(i)} ]. |  |  |  |  | 509447.5618 | 896163.6206 | 1084043.4514
11 |  | Total Estimated Cost excluding GST (Serial No. 5, 6, 7, 8, 9[ {A(i)}, {B(i)} ], 10) |  |  |  |  | 4585028.0564 | 8065472.5858 | 9756391.063
12 |  | Applicable CGST @ 9% on Serial No. 11 |  |  | 0.09 |  | 412652.5251 | 725892.5327 | 878075.1957
13 |  | Applicable SGST @ 9% on Serial No. 11 |  |  | 0.09 |  | 412652.5251 | 725892.5327 | 878075.1957
14 |  | Total estimated cost of S/s including GST (Serial No. 11+12+13). |  |  |  |  | 5410333.1065 | 9517257.6512 | 11512541.4543
15 |  | Total estimated cost of S/s including GST (Rounded off) |  |  |  |  | 5410333 | 9517258 | 11512541
Note: |  | (1) All the rates are with considering price variation clause.
(2) In case of non-availability of H-Beam for structure double welded RS Joist may be used and cost should be taken on actual material used
(3)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
Note on C95: Smt. Prarthana Shukla: Name Changed : Earlier was Incidental Charges @ 7.5% on Sub-Total - A : -

## B-4
COST SCHEDULE B-4
(33/11 kV SUB-STATIONS)
11 kV OUT DOOR YARD EXTENSION FOR ADDL. BAY WITH CIRCUIT BREAKER
2026-27
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | 1.6 MVA & Above
[6 empty] | Qnty | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | H-Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 No = 593.6 Kgs | 7130601958 | Kg | 53.0776 | 594 | 31528.0825
2 |  | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 52.6646 | 816 | 42974.2973
3 |  | MS DC Cross arm (100x50 mm), 5.2 Mtr long for bus bar | 7130810684 | Set | 9299.67 | 6 | 55798.02
4 |  | MS DC Cross arm (100x50 mm), 8' centre for bus bar | 7130810517 | Set | 5000.08 | 2 | 10000.16
5 |  | Clamp for “ H-Beam ” | 7130810692 | Pair | 362.75 | 15 | 5441.25
6 |  | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 101.05 | 48 | 4850.4
7 |  | Strain set with hardware suitable for 100 Sqmm ACSR conductor for 11 kV bus. |  | Set
| (i) | 33 kV Polymer Disc insulator for double disc | 7130820013 | No | 187.29 | 24 | 4494.96
| (ii) | Hardware suitable for 100 Sqmm ACSR Dog conductor for 11 kV bus. | 7130820248 | No | 333.97 | 24 | 8015.28
8 |  | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 378.54 | 3 | 1135.62
9 |  | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 327.8 | 3 | 983.4
10 |  | 11 kV Isolator (600 A.) | 7131930663 | Each | 26094.57 | 2 | 52189.14
11 |  | 11 kV AB Switch | 7131930221 | Each | 10471.34 | 1 | 10471.34
12 |  | R.S. Joist (175x85 mm) @ 2 mtr/Isolator | 7130600675 | Kg | 56.7279 | 78 | 4424.7801
13 |  | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 2.4 | 7128 | Material cost including GST and labour.
14 |  | ACSR 100 Sqmm Al. Eq. Dog Conductor | 7130830063 | Mtr | 120.4014 | 50 | 6020.0705
15 |  | Terminal clamp for jumpering of 100 Sqmm Al. Eq ACSR Conductor / Isolator | 7130830585 | No | 380.53 | 24 | 9132.72
16 |  | 11 kV feeder control VCB with CT's (One 11 kV VCB controlling two feeders) with control panel. |  | No | 231934.56 | 1
| (i) | 11 kV VCB (Without CT's & Panel) | 7131941762 | No | 154192.41 | 1 | 154192.41
| (ii) | 11 kV feeder Control Panel | 7131960008 | No | 28124.69 | 1 | 28124.69
| (iii) | 11 kV CT's 300-150/5 Amps | 7132230188 | No | 15178.97 | 3 | 45536.91
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No. | 4080.55 | 1 | 4080.55
17 |  | Concreting of foundation of VCB (1:3:6) | 7130200202 | Cmt | 2970 | 6 | 17820
18 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 253.2528 | 60 | 15195.168
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 132.305 | 120 | 15876.6024
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 72.3623 | 60 | 4341.7398
19 |  | H.T. STATIC TRIVECTOR METER for feeder metering. |  | No | 4787.15 | 1
|  | 3 Ø 4 Wire 0.5S, 5 Amp. with DLMS Protocol category A | 7131310033 | No | 4787.15 | 1 | 4787.15
20 |  | 11 kV CT/PT unit 200-100/5 Amp. | 7132230412 | Each | 46601.35 | 1 | 46601.35
21 |  | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 2 | 366.74
22 |  | Aluminium Paint | 7130210809 | Ltr | 409.72 | 2 | 819.44
23 |  | M.S. Nuts & Bolts |  | Kg |  | 30
| a | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 86.95 | 3 | 260.85
| b | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 85.5 | 2 | 171
| c | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 85.5 | 2 | 171
| d | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 84.05 | 6 | 504.3
| e | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 84.05 | 15 | 1260.75
| f | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 84.05 | 2 | 168.1
24 |  | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 594866.2706
25 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 504123.9581
26 |  | Incidental Charges @ 7.5% on Serial No. 25 :- |  |  |  | 0.075 | 37809.2969
27 | a | Services on Painting of structure |  | No | 5050.15 | 1 | 5050.15
| b | Const. of Brick masonary cable trench (Inside size 300 mm x 300 mm), with 200 mm thick walls and MS flat 40x5 mm @ 0.60 M c/c with standard drawings, i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 2155 | 5 | 10775
28 |  | Labour charges |  |  |  |  | 64968.5131
| i | as per Schedule No. BL-4 |  |  |  |  | 58749.9091
| ii | for concreting of structure |  | Cmt | 740.31 | 2.4 | 1776.744
| iii | for foundation of VCB |  | Cmt | 740.31 | 6 | 4441.86
29 |  | Transportation charges for all materials
| (i) | Transportation charges upto 100 km @ 2% of the cost of all Line materials excluding Civil Works. |  |  |  | 0.02 | 10082.4792
30 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 25, 26, 27, 28, 29[(i)]. |  |  |  |  | 79101.1747
31 |  | Total Estimated Cost Including Civil works but excluding GST (Serial No. 25, 26, 27, 28, 29[(i)], 30) |  |  |  |  | 711910.5719
32 |  | Applicable CGST @ 9% on Serial No. 31 |  |  |  | 0.09 | 64071.9515
33 |  | Applicable SGST @ 9% on Serial No. 31 |  |  |  | 0.09 | 64071.9515
34 |  | Total Estimated Cost including GST (Serial No. 31+32+33) |  |  |  |  | 840054.4748
35 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 840055
Note :- |  | (1)All the rates are with considering price variation clause.
(2)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
Note on C52: Smt. Prarthana Shukla: Name Changed : Earlier was Incidental Charges @ 7.5% on Sub-Total-1 : -

## B-5
COST SCHEDULE B-5
| (33/11 kV SUB-STATIONS) |  |  |  | 2026-27
33 kV OUT DOOR YARD EXTENSION FOR ADDITIONAL BAY.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H Beam 152x152 mm 37.1 kg/mtr 8 Mtr i.e. 296.8 kg/pole x 2 Nos = 593.6 Kgs | 7130601958 | Kg | 53.0776 | 594 | 31528.0825
2 | 11 Mtr long 152 x 152 mm H-Beam (37.1 Kg/ Mtr weight) i.e. 37.1 x 11 mtr = 408.1 kg/pole x 2 Nos = 816.2 Kgs. | 7130601965 | Kg | 52.6646 | 816 | 42974.2973
3 | MS DC cross arm (100x50 mm), 5.2 Mtr. long for bus bar | 7130810684 | Set | 9299.67 | 6 | 55798.02
4 | MS DC Cross arm (100 x 50 x 6 mm Channel) 3.8 Mtr long Set | 7130810006 | Set | 7486.37 | 2 | 14972.74
5 | Clamp for “ H-Beam ” | 7130810692 | Pair | 362.75 | 15 | 5441.25
6 | Strain Plate (65x8 mm) for 33 kV | 7130810624 | No. | 101.05 | 48 | 4850.4
7 | Strain set with hardware suitable for 80 Sqmm ACSR conductor for 33 kV bus (3 disc insulator per disc) |  | Set |  | 24
| (i) 33 kV Polymer Disc Insulator | 7130820013 | No | 187.29 | 24 | 4494.96
| (ii) 33 kV Hardware | 7130820248 | Each | 333.97 | 24 | 8015.28
8 | 33 kV Isolator (600 Amps.) without earth switch | 7131930752 | No | 45159.49 | 2 | 90318.98
9 | 33 kV Porcelain A.B. Switch | 7131930321 | Each | 23249.28 | 1 | 23249.28
10 | R.S. Joist (175x85 mm) @ 2 mtr/Isolator | 7130600675 | Kg | 56.7279 | 78 | 4424.7801
11 | Terminal clamp for isolators | 7130830585 | No | 380.53 | 12 | 4566.36
12 | T-clamps for bus jumper | 7130830585 | No | 380.53 | 6 | 2283.18
13 | ACSR 100 Sqmm Al. Eq. Conductor | 7130830063 | Mtr | 120.4014 | 50 | 6020.0705
14 | Concreting of structure (1:3:6) | 7130200202 | Cmt | 2970 | 2.4 | 7128 | Material cost including GST and labour.
15 | 33 kV Polymeric Pin insulator with Pin | 7130820009 | Each | 378.54 | 6 | 2271.24
16 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 2 | 366.74
17 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 2 | 819.44
18 | M.S. Nuts & Bolts |  | Kg |  | 40
| MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 86.95 | 2 | 173.9
| MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 85.5 | 3 | 256.5
| MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 85.5 | 5 | 427.5
| MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 84.05 | 15 | 1260.75
| MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 84.05 | 10 | 840.5
| MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 84.05 | 5 | 420.25
19 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 312902.5004
20 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 265171.6105
21 | Incidental Charges @ 7.5% on Serial No.- 20. |  |  | 0.075 |  | 19887.8708
22 | Services on Painting on structure |  | No | 5050.15 | 1 | 5050.15
23 | Labour charges as per Schedule No BL-5 |  |  |  |  | 34624.4
24 | Labour charges for concreting |  | Cmt | 740.31 | 2.4 | 1776.744
25 | Transportation charges for line all materials
(i) | Transportation charges upto 100 km @ 2% of the cost of Line all materials. |  |  | 0.02 |  | 5303.4322
26 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 20, 21, 22, 23, 24, 25[(i)] |  |  |  |  | 41476.7759
27 | Total Estimated Cost excluding GST (Row 20, 21, 22, 23, 24, 25[(i)], 26) |  |  |  |  | 373290.9834
28 | Applicable CGST @ 9% on Serial No. 27 |  |  | 0.09 |  | 33596.1885
29 | Applicable SGST @ 9% on Serial No. 27 |  |  | 0.09 |  | 33596.1885
30 | Total Estimated Cost including GST (Serial No. 27+28+29) |  |  |  |  | 440483.3605
31 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 440483
Note | (1)For the provision of 33 kV VCB installation, the cost Schedule No.- B-6 may be referred to. All the rates are with considering price variation clause
(2)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.

## B-6
COST SCHEDULE B-6
2026-27
INSTALLATION OF 33 kV VCB
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | 33 kV VCB with control panel & CT |  | No | 398337.6 | 1
| (i) | 33 kV VCB (without CT's & Panel) | 7131943380 | No | 280899.21 | 1 | 280899.21
| (ii) | 33 kV Control Panel | 7131960524 | No | 43018.74 | 1 | 43018.74
| (iii) | 33 kV CT's 300-150/5 Amps | 7132230263 | No | 24806.55 | 3 | 74419.65
| (iv) | Marshelling Box (with 10 No. connectors) | 7130352046 | No | 4080.55 | 1 | 4080.55
2 |  | Concreting of foundation of 33 kV breaker (1:3:6) | 7130200202 | Cmt | 2970 | 7 | 20790 | Material cost including GST and labour.
3 |  | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr | 120.4014 | 30 | 3612.0423
4 |  | Control cabling
| a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 253.2528 | 60 | 15195.168
| b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 132.305 | 120 | 15876.6024
| c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 72.3623 | 60 | 4341.7398
5 |  | Terminal clamps | 7130830585 | No | 380.53 | 6 | 2283.18
6 |  | Tee clamp for jumper | 7130830585 | No | 380.53 | 6 | 2283.18
7 |  | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 466800.0625
8 |  | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 395593.2733
9 |  | Incidental Charges @ 7.5% on Serial No. 8 :- |  |  | 0.075 |  | 29669.4955
10 |  | Labour charges for concreting |  | Cmt | 740.31 | 7 | 5182.17
11 |  | Labour charges as per Schedule No BL-6 |  |  |  |  | 20039.2
12 |  | Transportation charges for all materials
| (i) | Transportation charges upto 100 km @ 2% of the cost of all materials. |  |  | 0.02 |  | 7911.8655
13 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 08, 09, 10, 11, 12[(i)]. |  |  |  |  | 57299.5005
14 |  | Total Estimated Cost excluding GST (Serial No. 08, 09, 10, 11, 12[(i)], 13). |  |  |  |  | 515695.5048
15 |  | Applicable CGST @ 9% on Serial No. 14 |  |  | 0.09 |  | 46412.5954
16 |  | Applicable SGST @ 9% on Serial No. 14 |  |  | 0.09 |  | 46412.5954
17 |  | Total Estimated Cost including GST (Serial No. 14+15+16) |  |  |  |  | 608520.6957
18 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 608521
Note:- |  | (1)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
(2) All the rates are with considering price variation clause.
Note on C27: Smt. Prarthana Shukla: Name Changed: Earlier was Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 07, 09, 10, 11, 12

## B-8
COST SCHEDULE B-8
AUGMENTATION OF 33/11 kV SUB-STATION CAPACITY BY REPLACEMENT OF POWER TRANSFORMER
2026-27
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | 1.6 to 3.15 MVA |  | 3.15 to 5.0 MVA without 33 kV VCB |  | 3.15 to 5.0 MVA with 33 kV VCB
[5 empty] | Qnty | Amount | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 33/11 kV 3.15 MVA Power X-mer | 7132220095 | No | 4456033.02 | 1 | 4456033.02 | -- | -- | -- | --
2 | 33/11 kV 5.0 MVA Power X-mer | 7132220097 | No | 6078909.05 | -- | -- | 1 | 6078909.05 | 1 | 6078909.05
3 | 33 kV VCB (With CT's and control panel) |  | No |  | 1 |  | -- | -- | 1
| (i) 33 kV VCB (without CT's and panels) | 7131943380 | No | 280899.21 | 1 | 280899.21 |  |  | 1 | 280899.21
| (ii) 33 kV Control Panel | 7131960524 | No | 43018.74 | 1 | 43018.74 |  |  | 1 | 43018.74
| (iii) 33 kV CT's (300-150/5) Amps. oil filled | 7132230263 | No | 24806.55 | 3 | 74419.65 |  |  | 3 | 74419.65
4 | Concreting of foundation for 33 kV VCB (1:3:6) | 7130200202 | Cmt | 2970 | 7 | 20790 | -- | -- | 7 | 20790 | Material cost including GST and labour.
5 | Control cabling
a | 8 Core 2.5 Sqmm. (unarmoured) | 7130310658 | Mtr | 253.2528 | 60 | 15195.168 | 0 | 0 | 60 | 15195.168
b | 4 Core 2.5 Sqmm. (unarmoured) | 7130310654 | Mtr | 132.305 | 120 | 15876.6024 | 0 | 0 | 120 | 15876.6024
c | 2 Core 2.5 Sqmm. (unarmoured) | 7130310652 | Mtr | 72.3623 | 60 | 4341.7398 | 30 | 2170.8699 | 60 | 4341.7398
6 | Terminal clamp for transformer | 7130830586 | No | 304.09 | 7 | 2128.63 | 7 | 2128.63 | 7 | 2128.63
7 | T-clamps for jumper | 7130830586 | No | 304.09 | 6 | 1824.54 | -- | -- | 6 | 1824.54
8 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 4914527.3002 |  | 6083208.5499 |  | 6537403.3302
9 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 4164853.6442 |  | 5155261.483 |  | 5540172.3137
10 | Incidental Charges @ 7.5% on Serial No.9:- |  |  | 0.075 |  | 312364.0233 |  | 386644.6112 |  | 415512.9235
11 | Labour charges as per Schedule No BL-8 |  |  |  |  | 113421.53 |  | 113442.92 |  | 124940.63
12 | Labour charges for concreting |  | Cmt | 740.31 | 7 | 5182.17 | -- | -- | 7 | 5182.17
13 | Labour charges for installation of VCB (as per Schedule No. BL-6) |  |  | 20039.2 | 1 | 20039.2 |  |  | 1 | 20039.2
14 | Construction of Brick masonary cable trench (inside size 300 mm x 300 mm.), with 200 mm. thick walls and MS Flat 40x5 mm @ 0.60 M c/c with standard drawings, i/c all labour, T&P, transportation, loading, unloading, royalty etc. complete. |  | RM | 2155 | 5 | 10775 |  |  | 5 | 10775
15 | (A)Transportation of Power Transformer
(i) | Transportation charges upto 100 km @ 1% of the cost of 1.6 MVA, 3.15 MVA & 5 MVA Power Transformer |  |  | 0.01 |  | 37762.9917 |  | 51516.1784 |  | 51516.1784
(B)Transportation of all other materials excluding Power Transformer
(i) | Transportation charges upto 100 km @ 2% of the cost of all other materials excluding (a) Civil Works (b) PT of 1.6 MVA, 3.15 MVA & 5 MVA capacity |  |  | 0.02 |  | 7771.0895 |  | 72.8729 |  | 7771.0895
16 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. - 09, 10, 11, 12, 13, 14, 15[ {A(i)}, {B(i)} ]. |  |  |  |  | 584021.2061 |  | 713367.2582 |  | 771988.6881
17 | Total Estimated Cost excluding GST (Serial No. 09, 10, 11, 12, 13, 14, 15[ {A(i)}, {B(i)} ], 16) |  |  |  |  | 5256190.8548 |  | 6420305.3236 |  | 6947898.1933
18 | Applicable CGST @ 9% on Serial No. 17 |  |  | 0.09 |  | 473057.1769 |  | 577827.4791 |  | 625310.8374
19 | Applicable SGST @ 9% on Serial No. 17 |  |  | 0.09 |  | 473057.1769 |  | 577827.4791 |  | 625310.8374
20 | (-) Cost of Old Transformer assuming 25 years of life & 5 years in service. |  |  |  |  | 689731.848 |  | 1682037.0458 |  | 1682037.0458
21 | Total Estimated Cost of Augmentation including GST (Serial No. 17+18+19-20) |  |  |  |  | 5512573.3607 |  | 5893923.2361 |  | 6516482.8223
22 | Total Estimated Cost of Augmentation including GST (Rounded off) |  |  |  |  | 5512573 |  | 5893923 |  | 6516483
Note:- (1) All the rates are with considering price variation clause.
(2)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.
Note on B25: Smt. Prarthana Shukla: Name Changed : Earlier was Incidental Charges @ 7.5% on Sub-Total-1 : -
Note on B34: Smt. Prarthana Shukla: Name Changed: Earlier was Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Row - 08, 10, 11, 12, 13, 14, 15, 16
Note on G38: Rate of FY 2013-14 considered
Note on I38: Rate of FY 2013-14 considered
Note on K38: Rate of FY 2013-14 considered

## B-9
` |  | COST SCHEDULE B-9
INSTALLATION OF 1.6 MVA 33/11 kV SUB-STATION ON LINE
2026-27
S. No. | PARTICULARS |  | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 |  | 3 | 4 | 5 | 6 | 7
1 |  | CIVIL WORKS (Rate as per SoR PWD)
| 1 | Land |  | Sq Mtr | LS
| 2 | Construction of 1.50 Mtr high barbed wire fencing in angle iron post as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, etc. complete. |  | Mtr | 406 | 32 | 12992
| 3 | Construction of 4.50 m x 2.15 m size yard / area gate as per given drawing including all labour, T&P, curing, materials, transportation, loading, unloading, royalty, etc. complete. |  | Each | 36900 | 1 | 36900
| 4 | Total of 01 : - |  |  |  |  | 49892
2 |  | EQUIPMENTS AND BUS BAR ARRANGEMENT
| 1 | Power Transformer 1.6 MVA | 7132220091 | No | 1500128.26 | 1 | 1500128.26
| 2 | PCC supports 280 Kg; 9.1 Mtr. long | 7130800033 | No | 4613.69 | 2 | 9227.38
| 3 | 33 kV "V" cross arm | 7130810595 | No | 2564.36 | 2 | 5128.72
|  | (i) Cross arm clamp | 7130810361 | Pair | 347.95 | 2 | 695.9
| 4 | 33 kV Top clamp | 7130810676 | No | 426.66 | 5 | 2133.3
| 5 | 33 kV Porcelain A.B. Switch | 7131930321 | Each | 23249.28 | 1 | 23249.28
| 6 | 33 kV D.O. Fuse Unit | 7131930415 | Each | 3310.46 | 3 | 9931.38
| 7 | 33 kV Porcelain Lightning Arrestors | 7130840021 | Each | 4289.09 | 3 | 12867.27
| 8 | 33 kV Polymeric Pin Insulator with Pin | 7130820009 | Each | 378.54 | 9 | 3406.86
| 9 | MS Channel 100x50 mm, 5.2 Mtr. Long for D.O., A.B. switch and LA mounting. | 7130810684 | No | 9299.67 | 2 | 18599.34
| 10 | PCC supports 140 Kg; 8.0 Mtr. for 11 kV Bus | 7130800012 | No | 2371.18 | 8 | 18969.44
| 11 | MS Channel 5.2 Mtr. long | 7130810684 | No | 9299.67 | 16 | 148794.72
| 12 | 11 kV AB Switch complete | 7131930221 | Each | 10471.34 | 3 | 31414.02
| 13 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 327.8 | 3 | 983.4
| 14 | 11 kV Strain set with hardware |  | Set |  | 21
|  | 11 kV Polymer Disc insulator | 7130820010 | No | 111.39 | 21 | 2339.19
|  | 11 kV Hardware | 7130820241 | No | 160.75 | 21 | 3375.75
| 15 | ACSR Conductor 80 Sqmm Al. Eq. Raccoon Conductor | 7130830060 | Mtr. | 89.5109 | 20 | 1790.2188
| 16 | T-clamps for Raccoon Conductor | 7130830586 | No | 304.09 | 27 | 8210.43
| 17 | Bimetallic Clamps for Transformer & auto recloser | 7130830052 | No | 1055.83 | 12 | 12669.96
| 18 | Red Oxide Paint | 7130211158 | Ltr | 183.37 | 5 | 916.85
| 19 | Aluminium Paint | 7130210809 | Ltr | 409.72 | 5 | 2048.6
| 20 | M.S. Nut- Bolts |  | Kg |  | 125
|  | MS Nuts and bolts 16x40 mm | 7130620609 | Kg | 86.95 | 2 | 173.9
|  | MS Nuts and bolts 16x65 mm | 7130620614 | Kg | 85.5 | 2 | 171
|  | MS Nuts and bolts 16x90 mm | 7130620619 | Kg | 85.5 | 25 | 2137.5
|  | MS Nuts and bolts 16x160 mm | 7130620627 | Kg | 84.05 | 40 | 3362
|  | MS Nuts and bolts 16x200 mm | 7130620631 | Kg | 84.05 | 50 | 4202.5
|  | MS Nuts and bolts 16x250 mm | 7130620637 | Kg | 84.05 | 6 | 504.3
| 21 | M.S. Flat 50x6 mm | 7130600173 | Kg | 51.0754 | 100 | 5107.541
| 22 | Earthing of Sub-station
|  | (i) G.I. Pipe of 40 mm dia. 3.04 Mtr. long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 870.41 | 12 | 10444.92
|  | (ii) MS flat 50x6 mm size | 7130600173 | Kg | 51.0754 | 60 | 3064.5246
|  | (iii) G.I. Wire 8 SWG | 7130870043 | Kg | 69.8234 | 10 | 698.2335
|  | (iv) G.I. Nuts and bolts 16x40 mm | 7130620133 | Kg | 120.28 | 5 | 601.4
|  | (v) G.I. Nuts and bolts 16x65 mm | 7130620140 | Kg | 120.28 | 4 | 481.12
|  | (vi) G.I. Spring washers | 7130622922 | Kg | 152.82 | 1 | 152.82
| 23 | SUB TOTAL-1 [of Row - 2 (Material cost including GST)] |  |  |  |  | 1847982.0279
3 |  | Material cost excluding GST [for Row - 2 (Sub Total-1/1.18)] |  |  |  |  | 1566086.4643
4 |  | Incidental Charges @ 7.5% on Serial No. - 3 : - |  |  | 0.075 |  | 117456.4848
5 |  | Services On Earthing of sub-station. |  | No | 3892.54 | 1 | 3892.54
6 |  | Labour charges as per Schedule No BL-9 |  |  |  |  | 134086.51
7 | (A) | Transportation of Power Transformer
| (i) | Transportation charges upto 100 km @ 1% of the cost of 1.6 MVA Power Transformer |  |  | 0.01 |  | 12712.9514
| (B) | Transportation of all other materials excluding Power Transformer
| (i) | Transportation charges upto 100 km @ 2% of the cost of all other materials excluding (a) Civil Works; (b) PT of 1.6 MVA capacity. |  |  | 0.02 |  | 5895.8266
8 |  | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial No. 01(04) ,03, 04, 05, 06,07[ {A(i)}, {B(i)} ]. |  |  |  |  | 236252.8471
9 |  | Total Estimated Cost including civil works excluding GST (Serial No. 01(04), 03, 04, 05, 06,07[ {A(i)}, {B(i)} ], 08) |  |  |  |  | 2126275.6242
10 |  | Applicable CGST @ 9% on Serial No. 8 |  |  | 0.09 |  | 191364.8062
11 |  | Applicable SGST @ 9% on Serial No. 8 |  |  | 0.09 |  | 191364.8062
12 |  | Total Estimated Cost including GST (Sr. No. 9+10+11) |  |  |  |  | 2509005.2366
13 |  | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 2509005
Note:- |  | (1) All the rates are with considering price variation clause.
(2)Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.

## B-10
COST SCHEDULE B-10
SCHEDULE FOR 33/11 SUB-STATION CHEMICAL EARTHING
2026-27
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Soil excavation through Manual machine |  | Soil excavation through Boring Machine
[5 empty] | Qnty | Amount | Qnty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | Copper Bonded Rod 25mm 3 Mtr long * | 7130870011 | No. | 16763.9606 | 2 | 33527.9212 | 2 | 33527.9212 | Value in bincode GST excluded, so GST @ 18% added
2 | Copper Bonded Rod 17.2mm, 3 Mtr long ** | 7130870012 | No. | 13536.7358 | 8 | 108293.8864 | 8 | 108293.8864 | Value in bincode GST excluded, so GST @ 18% added
3 | COMPOUND (1 packet of 25 kg) 2 packet per earth pit | 7132490002 | Packet | 1596.9884 | 20 | 31939.768 | 20 | 31939.768 | Value in bincode GST excluded, so GST @ 18% added
4 | Copper bonded strip 25x3 mm (0.65kg/Mtr) | 7130870014 | Mtr. | 393.4592 | 200 | 78691.84 | 200 | 78691.84 | Value in bincode GST excluded, so GST @ 18% added
5 | G.I.Nots & Bolts 16x40 mm | 7130620133 | kg | 120.28 | 1.5 | 180.42 | 1.5 | 180.42
6 | G.I.Nots & Bolts 16x55 mm | 7130620140 | kg | 120.28 | 1.5 | 180.42 | 1.5 | 180.42
7 | G.i spring Washer | 7130622922 | kg | 152.82 | 1 | 152.82 | 1 | 152.82
8 | ACSR conductor 100 Sqmm Al Eq. (Dog) | 7130830063 | Mtr. | 120.4014 | 150 | 18060.2115 | 150 | 18060.2115
9 | Bimetallic Clamp | 7130830056 | No. | 616.6 | 16 | 9865.6 | 16 | 9865.6
10 | SUB TOTAL-1 (Material cost including GST) |  |  |  |  | 280892.8871 |  | 280892.8871
11 | Material cost excluding GST (Sub Total-1/1.18) |  |  |  |  | 238044.8196 |  | 238044.8196
12 | Incidental Charges @ 7.5% on serial no 11 |  |  | 0.075 |  | 17853.3615 |  | 17853.3615
13 | Labour Charges as per proposed labour schedule CL-23 |  | No. |  | 1 | 25576.59 | 1 | 29032.3665
14 | LABOUR FOR DIGGING |  |  | 2572.5 | 4 | 10290 | 4 | 10290
15 | Transportation charges of all line materials
(i) | Upto 100 km @ 2% on Serial no. 11 |  |  | 0.02 |  | 4760.8964 |  | 4760.8964
16 | Overhead Charges @ 12.5% [Market Fluctuation, Service Tax, Contractor's profit etc.] on Serial no. -11, 12, 13, 14, 15(i) |  |  |  |  | 37065.7084 |  | 37497.6805
17 | Total Estimated Cost excluding GST (serial no - ( 11,12,13,14,15(i),16) |  |  |  |  | 333591.3758 |  | 337479.1244
18 | Applicable CGST @ 9% on Serial no. 17 |  |  | 0.09 |  | 30023.2238 |  | 30373.1212
19 | Applicable SGST @ 9% on Serial no. 17 |  |  | 0.09 |  | 30023.2238 |  | 30373.1212
20 | Total Estimated Cost including GST (Serial no. 17+18+19) |  |  |  |  | 393637.8235 |  | 398225.3668
21 | Total Estimated Cost including GST (Rounded off) |  |  |  |  | 393638 |  | 398225
Note:- | * for transformer body and neutral earthing
** for earthing of rest of the points
Transportation charges of line materials are calculated in this schedule "up to 100 km only" for "PURE REFERENCE". Officers are advised to take the reference of Important instruction for SoR 25-26 for calculation of transportation charges as per their actual field conditions while preparing the estimates.