## SOR RATE
RATE OF STOCK MATERIALS IN 2016-17
Material Code | Description | unit | Unit rate for 2016-17 | SAP DESCRIPTION
7130200201 | 1:1.5:3 Ratio | Cmt | 3940
7130200202 | 1:3:6 Ratio | Cmt | 3079
7130200204 | Route & joint indicating stone with M.S. anchor rod | Nos. | 157 | ROUTE & JOINT INDICATING STONE WITH M.S.
7130200401 | Cement in 50 kg bags | Bags | 245 | Cement
7130201343 | Cable covering tiles 250x250x40 mm | Per 1000 | 10423
7130210809 | Aluminium Paint | Ltr. | 297 | Aluminium Paint.
7130211121 | Grey Enamel Paint smoke/battle ship | Ltr | 223
7130211158 | Red Oxide Paint | Ltr. | 133 | Red Oxide Paint.
7130300025 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X70+1x16+1x50 | km | 202527 | LT AB CABLE 3X70+1X16 (STREET LIGHT)+1X5
7130310007 | 70 Sqmm. | Km. | 39435 | ISI MARKED CABLE ALU 1CORE 70 SQMM 1100V
7130310008 | 120 Sqmm. | Km. | 75161 | ISI MARKED CABLE ALU 1CORE 120 SQMM 1100
7130310020 | 3x400 Sq.mm. | km | 2066592 | 33KV 400 sqmm XLPE cable (Underground)
7130310021 | 35 Sqmm. | Km. | 24976 | ISI MARKED CABLE ALU 1CORE 35 SQMM 1100V
7130310022 | 50 Sqmm. | Km. | 31637 | ISI MARKED CABLE ALU 1CORE 50 SQMM 1100V
7130310031 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X16+1X16+1x25 | km | 54240 | 1.1KV LT AB CABLE 3X16+1X16+1X25 SQMM
7130310032 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X25+1X16+1x25 | km | 69001 | 1.1KV LT AB CABLE 3X25+1X16+1X25 SQMM
7130310033 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X35+1x16+1x25 | km | 85822 | 1.1KV LT AB CABLE 3X35+1X16+1X25 SQMM
7130310038 | 2.5 Sqmm. | Per Mtr. | 6 | 11KV PVC INSULATED 2.5 SQMM TWIN CORE SI
7130310039 | 6.0 Sqmm. | Per Mtr. | 26 | 11KV PVC INSULATED 6 SQMM TWIN CORE SING
7130310040 | 10 Sq.mm. | Per Mtr. | 54 | 11KV PVC INSULATED 10 SQMM FOUR CORE THR
7130310041 | 150 Sqmm. | Km. | 97435 | 11KV PVC INSULATED 150SQMM SINGLE CORE X
7130310042 | 16.0 Sqmm. | km | 34886 | 11KV PVC INSULATED 16SQMM 2 CORE ARMOURE
7130310044 | 10 Sq.mm. | km | 49565 | 11KV PVC INSULATED 10SQMM 4 CORE ARMOURE
7130310048 | 25 Sq.mm. | km | 76318
7130310049 | 120 Sq.mm. | km | 327469
7130310050 | 400 Sqmm. | km | 911817
7130310051 | 3x95 Sq.mm. | km | 826257 | 33KV A.B. XLPE CABLE 3X95 SQMM
7130310052 | 3x150 Sq.mm. | km | 1014277
7130310053 | 3x185 Sq.mm. | km | 1159278 | 33KV A.B. XLPE CABLE 3X185 SQMM
7130310054 | 3x240 Sq.mm. | km | 1474142 | 33KV A.B. XLPE CABLE 3X240 SQMM
7130310055 | 33 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 17336
7130310056 | 33 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 24765
7130310057 | 11 kV 3 phase Aerial Bunched Cable 3x35 + 35 Sq mm | km | 281789 | 11KV 3 PHASE AERIAL BUNCHED XLPE CABLE 3
7130310058 | 11 kV 3 phase Aerial Bunched Cable 3x70 + 70 Sq mm | km | 398660
7130310059 | 11 kV 3 phase Aerial Bunched Cable 3x95 + 95 Sq mm | km | 596108
7130310060 | 11 kV 3 phase Aerial Bunched Cable 3x120 + 120 Sq mm | km | 562278
7130310061 | 11 kV AB Cable Straight thru' joint kit suitable for 35-70 sqmm | Set | 3784 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310062 | 11 kV AB Cable Straight thru' joint kit suitable for 95-120 sqmm | Set | 3982 | 11KV AB XLPE CABLE STRAIGHT THRU JOINT K
7130310063 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X25+1X16+1x25 | km | 46229 | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310064 | LT 1 phase 3 Wire Aerial Bunched Cable of Size 1X35+1X16+1x25 | km | DELETED | LT 1PH 3 WIRE AERIAL BUNCHED CABLE OF SI
7130310065 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1x16+1x35 | km | 113368 | 1.1KV LT AB CABLE 3X50+1X16+1X35 SQMM
7130310066 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X50+1X25+1x35 | km | 123854 | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310067 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x50 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310068 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x16+1x70 | km | DELETED
7130310069 | LT 3 phase 5 Wire Aerial Bunched Cable of Size 3X95+1x35+1x70 | km | DELETED | LT 3PH 5 WIRE AERIAL BUNCHED CABLE OF SI
7130310070 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X16+1x25 | km | 45159 | LT AB CABLEB 3X16+1X25 SQMM
7130310073 | LT 3 phase 4 Wire Aerial Bunched Cable of Size 3X25+1x25 | km | 60003 | LT AB CABLEB 3X25+1X25 SQMM
7130310075 | 3x240 Sq.mm. | km | 1891074 | 33KV 3 CORE XLPE UG CABLE 3X 240SQMM
7130310076 | 70 Sq.mm | km | 504670
7130310077 | 95 Sq.mm | km | 510601 | 11KV 3 CORE XLPE UG CABLE 95 SQMM
7130310078 | 120 Sq.mm | km | 761409 | 11KV 3 CORE XLPE UG CABLE 120 SQMM
7130310079 | 240 Sq.mm | km | 922530 | 11KV 3 CORE XLPE UG CABLE 240 SQMM
7130310080 | 400 Sq.mm | km | 1421382 | 11KV 3 CORE XLPE UG CABLE 400 SQMM
7130310652 | 2 Core (UNARMOURED) | Km. | 35395 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310652 | 2 Core (ARMOURED) | Km. | 65704 | CONTROL CABLE COP 2CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (UNARMOURED) | Km. | 58843 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310654 | 4 Core (ARMOURED) | Km. | 94649 | CONTROL CABLE COP 4CORE 2.5SQMM PVC/PVC
7130310658 | 8 Core (UNARMOURED) | Km. | 106359 | CONTROL CABLE COP 8 CORE 2.5 SQ MM PVC/P
7130310660 | 10 Core (UNARMOURED) | Km. | 132115 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310660 | 10 Core (ARMOURED) | Km. | 144477 | CONTROL CABLE COP 10CORE 2.5SQMM PVC/PVC
7130310662 | 12 Core (UNARMOURED) | Km. | 143554 | CONTROL CABLE COP 12CORE 2.5SQMM PVC/PVC
7130311008 | 16 Sq.mm. | KM | 14819 | ALUMINIUM 1C 16 SQ MM UNARMOURED LT PVC
7130311009 | 50 Sq.mm. | KM | 34517 | ALUMINIUM 1C 50 SQ MM UNARMOURED LT PVC
7130311010 | 70 Sq.mm | KM | 46364 | ALUMINIUM 1C 70 SQ MM UNARMOURED LT PVC
7130311011 | 150 Sq.mm | KM | 87502 | ALUMINIUM 1C 150 SQ MM UNARMOURED LT PVC
7130311012 | 300 Sq.mm | KM | 169478 | ALUMINIUM 1C 300 SQ MM UNARMOURED LT PVC
7130311013 | 400 Sq.mm | KM | 209245 | ALUMINIUM 1C 400 SQ MM UNARMOURED LT PV
7130311054 | 70 Sqmm. | km | 114082 | POWERCABLE ARM ALU 3.5CORE 70/35SQMM PVC
7130311057 | 150 Sqmm. | km | 394640 | POWERCABLE ARM ALU 3.5CORE 150/70SQMM PV
7130311061 | 300 Sqmm. | km | 626228 | Power Cable ARM ALU 3.5CORE 300/150SQMM
7130311084 | 16.0 Sqmm. | km | 52156 | 16,0 SQMM, 4 CORE, ARMOURED AL. CABLE
7130320037 | 33 kV ABC Termination kit 35-70 sqmm | Set | 9906
7130320038 | 33 kV ABC Termination kit 95-120 sqmm | Set | 12383 | 33KV ABC TERMINATION KIT 95-120 SQMM
7130320039 | 33 kV ABC Termination kit 185 sqmm | Set | 14859 | 33KV ABC TERMINATION KIT 185 SQMM
7130320040 | 33 kV ABC Termination kit 240 sqmm | Set | 17336 | 33KV ABC TERMINATION KIT 240 SQMM
7130320041 | 33 kV ABC Termination kit 300 sqmm | Set | 18574
7130320042 | 33 kV ABC Termination kit 400 sqmm | Set | 22289
7130320043 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 780 | STRAIGHT LINE SUSPENSION ASSEMBLY FOR AL
7130320044 | Dead-end Assembly (Suitable for all size cable) | Each | 842
7130320045 | Cable tie for AB Cable | Each | 25
7130320046 | 11 kV ABC-T Jointing kit 35-70 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 35-70 SQMM
7130320047 | 11 kV ABC-T Jointing kit 95-120 sqmm | Set | DELETED | 11KV ABC T-JOINTING KIT 95-120 SQMM
7130320048 | 11 kV ABC Termination kit 35-70 sqmm | Set | 2396 | 11KV ABC TERMINATION KIT 35-70 SQMM
7130320049 | 11 kV ABC Termination kit 95-120 sqmm | Set | 2524
7130320053 | Cable tie (UV protected black colour) for AB Cable | No | 5 | CABLE TIE FOR AB CABLE (UV PROTECTED BLA
7130352010 | End terminating jointing kit for 400 sqmm XLPE cable | Set | 35084 | Jointing kit 33KV 3x400sqmm XLPE cable
7130352030 | 10 Sq.mm, 4 Core | Set | 804
7130352031 | 16 Sq.mm, 4 Core | Set | 804 | 1.1KV STRAIGHT THROUGH JOINTING KIT FOR
7130352032 | 25 Sq.mm, 4 Core | Set | 863
7130352033 | 70 Sq.mm, 3.5 Core | Set | 1213
7130352034 | 150 Sq.mm, 3.5 Core | Set | 1808
7130352035 | 300 Sq.mm, 3.5 Core | Set | 2923
7130352036 | 400 Sq.mm, 3.5 Core | Set | 3735
7130352037 | End terminating jointing kit for 240 sqmm XLPE cable | Set | 21050 | 33KV END TERMINAL JOINTING KIT FOR 240SQ
7130352038 | 3x70 Sq.mm | Set | 7880
7130352039 | 3x95 Sq.mm | Set | 8701 | 3X95 SQMM 11KV HEAT SHRINKABLE TYPE JOIN
7130352040 | 3x150 Sq.mm | Set | 10187 | 3X150 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352041 | 3x240 Sq. mm | Set | 10751 | 3X240 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352042 | 3x400 Sq. mm | Set | 11000 | 3X400 SQMM 11KV HEAT SHRINKABLE TYPE JOI
7130352043 | 3x95 Sq.mm | Set | 2406 | 3X95 SQMM 11KV HEAT SHRINKABLE INDOOR TY
7130352044 | 3x240 Sq. mm | Set | 2561 | 3X240 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352045 | 3x400 Sq. mm | Set | 2630 | 3X400 SQMM 11KV HEAT SHRINKABLE INDOOR T
7130352046 | Marshelling Box | No. | 3115 | MARSHELLING BOX
7130354274 | 10 Sq mm | Nos. | 2 | 10 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354275 | 16 Sq mm | Nos. | 2 | 16 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354276 | 25 Sq mm | Nos. | 4
7130354277 | 32 Sq mm | Nos. | 5
7130354278 | 50 Sq mm | Nos. | 8 | 50 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354279 | 70 Sq mm | Nos. | 12 | 70 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354280 | 95 Sq mm | Nos. | 15 | 95 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354281 | 120 Sq mm | Nos. | 21 | 120 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354282 | 150 Sq mm | Nos. | 24 | 150 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354283 | 185 Sq mm | Nos. | 38
7130354284 | 225 Sq mm | Nos. | 43
7130354285 | 240 Sq mm | Nos. | 61
7130354286 | 300 Sq mm | Nos. | 72 | 300 SQMM ALUMINIUM END TERMINALS (LUGS)
7130354287 | 400 Sq mm | Nos. | 93
7130354442 | Pre-Insulated Bimetallic crimping lugs for Transformer connector | Nos. | 627 | PRE- INSULATED BIMETALLIC CRIMPING TYPE
7130390003 | Piercing connector suitable for 95- 16 sqmm to 10-2.5 sqmm. for street light and service connection. | Nos. | 80 | INSULATING PIERCING CONNECTOR AB CABLE(S
7130390004 | Piercing connector suitable for 95- 16 sqmm to 50-16 sqmm. cable for Distribution Box. | Nos. | 104 | INSULATING PIERCING CONNECTOR FOR AB CAB
7130390005 | Piercing connector suitable for 95- 16 sqmm to 95-16 sqmm. for Tee connection. | Nos. | 145 | INSULATING PIERCING CONNECTOR FOR ABC TO
7130390006 | Universal distribution connector | Each | 149 | UDC- UNIVERSAL DISTRIBUTION CONNECTOR
7130390007 | Straight through joints | Nos. | 172 | STRAIGHT THROUGH JOINT
7130390008 | Piercing connector for services 16-50 Sq. mm Tap off 2.5-16 Sq. mm | Each | DELETED
7130390017 | Suspension Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390018 | Tension/Dead end Clamp Assembly with Hook bracket & Pole Clamp | Each | DELETED
7130390019 | End cap for 50/70 Sq.mm | Nos. | 28 | END CLAMP CAP FOR 50/70 SQMM
7130600023 | 50 x 50 x 6 mm | MT | 33236 | M S ANGLE 50X50X5 MM
7130600032 | 65 x 65 x 6 mm | MT | 33236 | M S ANGLE 65X65X6 MM
7130600051 | 75 x 75 x 6 mm | MT | 33236 | M S ANGLE 75X75X6 MM
7130600075 | Angle line Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing kit 11KV ABC Cabl 3x25+1x35sqmm
7130600166 | 75x40 mm | MT | 33236 | M S CHANNEL 75X40 MM CP
7130600173 | 50x6 mm | MT | 34149 | M.S.FLATE 50X6 MM CP
7130600230 | 100x50 mm | MT | 33236 | M S CHANNEL 100X50 MM
7130600495 | 65x8 mm | MT | 34149 | M S FLAT 65X8 MM
7130600635 | 125 x 70 mm | MT | 28651 | R.S.JOIST 125 x 70 mm
7130600675 | 175 x 85 mm | MT | 32575 | R S JOIST 175X85 MM
7130601070 | 52 kgs per mtr/105 lbs yard | MT | 47797 | Rails 52.09 kgs per Mtr./105 lbs yard
7130601072 | 60 kgs per mtr | MT | 47797 | RAIL 60 KG PER METER
7130601958 | 37.1 Kg/Mtr.; 13 Mtr. Length | MT | 32575 | H BEAMS 152X152MM; 37,1 KG/MTR.
7130601965 | 37.1 Kg/Mtr.; 11 Mtr. Length | MT | 32575 | MS H BEAMS 152X152MM, 37.1 KG/MTR 11MTR
7130610206 | Barbed wire | MT | 63963 | G.I. WIRES: - Barbed wire.
7130620013 | I-Bolt (big size) | No | 116.46 | I BOLT M 20X128MM THREAD PORTION 50 MM I
7130620049 | 12x65 mm | Kg | 63
7130620133 | 16x40 mm | Kg | 87 | BOLT WITH NUT G I 16X40 MM
7130620140 | 16x65 mm | Kg | 87 | BOLT WITH NUT GI 16X65 MM
7130620573 | 12x100 mm | Kg | 63 | BOLT WITH NUT M S 12X100 MM
7130620575 | 12x120 mm | Kg | 64 | M S NUTS AND BOLTS: - 12x120mm
7130620577 | 12x140 mm | Kg | 64 | M S NUTS AND BOLTS: - 12x140mm
7130620609 | 16x40 mm | Kg | 63 | M S NUTS AND BOLTS: - 16x40mm
7130620614 | 16x65 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x65mm
7130620619 | 16x90 mm | Kg | 62 | M S NUTS AND BOLTS: - 16x90mm
7130620621 | 16x100 mm | Kg | 61 | M S NUTS AND BOLTS: - 16x100mm
7130620625 | 16x140 mm | Kg | 61 | M S NUTS AND BOLTS: - 16x140mm
7130620627 | 16x160 mm | Kg | 61 | M S NUTS AND BOLTS: - 16x160mm
7130620631 | 16x200 mm | Kg | 61 | M S NUTS AND BOLTS - 16x200mm
7130620636 | 16x300 mm | Kg | 61 | M S NUTS AND BOLTS: - 16x300mm
7130620637 | 16x250 mm | Kg | 61 | M S NUTS AND BOLTS: - 16x250mm
7130620713 | 20x75 mm | Kg | 61 | M S NUTS AND BOLTS: - 20x75mm
7130620716 | 20x90 mm | Kg | 61 | M S NUTS AND BOLTS: - 20x90mm
7130620719 | 20x110 mm | Kg | 61 | M S NUTS AND BOLTS: - 20x110mm
7130620829 | 24x120 mm | Kg | 61 | M S NUTS AND BOLTS: - 24x120mm
7130621892 | Foundation bolt | No | 389.83 | Foundation bolt 25x1200 mm
7130622922 | G.I. Spring Washer | Kg | 125 | WASHER SPRING 25MM HOLE DIA
7130640027 | G.I. Pipe 200 mm for 400 mm cable of dia 105 mm | RM | 929 | G.I. PIPE 200 MM FOR 400 MM CABLE OF DIA 1
7130640028 | G.I. bend 200 mm | Nos. | 805 | G.I.BEND 200MM
7130640029 | Caping of HDPE Pipe on both end of pipe with concreting and bricks work. | Cmt | 3220 | CAPING OF HDPE PIPE ON BOTH END OF PIPE
7130640030 | 600 mm | Each | 3857
7130640036 | 900 mm | Each | 7661 | 900 MM RCC PIPE TYPE NP-2(2.5MTR LONG)
7130640037 | M.S.Pipe 200 mm dia with collars | RM (light) | 862 | M.S. PIPE 200MM DIA WITH COLLARS
7130641396 | Gl Pipe 40 mm | Per Mtr | 179 | PIPE GI 40 MM MEDIUM QUALITY
7130642039 | GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | No | 770 | G.I. EARTHING PIPE 40 MM
7130642041 | 25 mm dia 2500 mm long GI rod earth electrodes | No | 3914 | G.I.EARTHING PIPE/ROD SIZE 2500x25 mm
7130650001 | Providing, Fabricating and fixing 8 SWG Chain link fencing (TATA Make) 75 x 75 mm Size Gl Chain link Mesh fencing made out of 65 x 65 x 6 mm MS angle as per drawing no. T&D/DRG/MISC/2 Revision -2 | Sq.mtr | 1131
7130670027 | Wall mounting type holder for Hydrometer | Nos. | 119
7130797532 | Anchor clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 599 | ANCHOR CLAMP/ DEAD END CLAMP
7130797533 | Suspension clamp assembly (consisting of GI Pole Clamp, GI Flat type I-hook & Nylon Cable tie). | Nos. | 435 | SUSPENSION CLAMP
7130797533 | Suspension Clamp (Suitable for all size cable) | Each | DELETED | SUSPENSION CLAMP
7130800012 | 140 Kg; 8.0 Mtr long | Each | 1659 | PCC POLE 140 KG; 8,0 MTR LONG
7130800014 | 410-SP-29, 9 Mtrs. Long. | Each | 6015
7130800033 | 280 Kg; 9.1 Mtr long | Each | 2993 | PCC POLE 280 KG; 9,1 MTR LONG
7130800068 | 410-SP-60, 12 Mtrs. Long. | Each | 10079 | POLE-STEEL TUBULAR 100X125X150MM 10.9 MT
7130800672 | 350 Kg; 7.0 Mtr long | Each | 2623 | PCC POLE 350 KG; 7,0 MTR LONG
7130810005 | Through Bolt | No | 81.91 | Through Bolt 12 mm
7130810006 | D.C. Cross arm 3.8 Mtr 100 x 50 mm. | Set | 5626.81 | D.C. Cross arm 3.8 Mtr 100 x 50 mm.
7130810026 | Stay clamp for 140 kG PCC Pole | Pair | 120.59 | Stay clamp LT/Pair
7130810026 | Stay clamp HT per pair | Pair | 225.04 | Stay clamp LT/Pair
7130810060 | LT U CLAMP | No. | 60.29 | LT U CLAMP
7130810076 | Strain Plate (50x6 mm) for 11 kV | No. | 57 | Strain Plate
7130810077 | Pole Clamp | No. | 394 | POLE CLAMP
7130810102 | Service Ring | No. | 349 | Service ring made of 16 mm
7130810193 | Stay Clamp for 280 kG. PCC Pole | Pair | 225.04 | HT STAY CLAMP PCC POLE 280 KG A TYPE
7130810201 | Stay Clamp Rail "A" type | Pair | 239.47 | HT STAY CLAMP RAIL POLE A TYPE
7130810216 | Stay Clamp for R.S.Joist "A" type | Pair | 239.47 | HT STAY CLAMP R S JOIST A TYPE
7130810251 | Stay Clamp Rail "B" type | Pair | 239.47 | HT STAY CLAMP RAIL POLE B TYPE
7130810361 | Back Clamp Rail for H-Beam | Pair | 239.47 | 33 KV TOP CLAMP SEMIFINISHED
7130810413 | L.T. 3 Pin Cross Arm 50x50x6 mm | No. | 510.78 | LT THREE PIN CROSS ARM
7130810441 | L.T. 4 Pin Cross Arm 50x50x6 mm | No. | 608.3 | 713081LT 4-Pin cross arms 50 x 50 x 6 mm
7130810461 | L.T. 5 Pin Cross Arm 50x50x6 mm | No. | 705.83 | LT FIVE PIN CROSS ARM
7130810495 | 11 kV Cross Arm Cleat type | No. | 866.17 | 11 KV V CROSS ARM
7130810509 | Lightning Arrestor Structure | No. | 6483.89 | D.O. / LA Mounting channel 75x40 mm.
7130810509 | D.O. Mounting Channel 75x40 mm | No. | 2745.63 | D.O. / LA Mounting channel 75x40 mm.
7130810511 | 11 kV Guarding Channel 100x50 mm | Set | 2053.85 | 1.1 MTR DPDC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 100x50 mm Channel 2 Nos. | Set | 3256.41 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre 75x40 mm Channel | Set | 2365.44 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810512 | D.C.Cross arm 4' Centre Angle 100x100x6 mm | Set | 3324.18 | 11KV 4 FEET CENTRE DC CROSS ARM
7130810517 | D.C.Cross arm 8' Centre 100x50 mm Channel | Set | 3758.1 | 11KV 8 FEET CENTRE DC CROSS ARM
7130810595 | 33 kV Cross Arm 75x75x6 mm | No. | 1927.4 | 33 KV V CROSS ARM
7130810608 | D.C.Cross arm 5' Centre 100x50 mm M.S.Channel | Set | 4444.09 | 33 KV 5 FEET CENTRE DC CROSS ARM
7130810624 | Strain Plate (65x8 mm) for 33 kV | No. | 75 | STRAIN PLATE
7130810624 | Strain Plate | Set | 92.77 | STRAIN PLATE
7130810676 | 33 kV Top Channel 75x75x6 mm | No. | 320.68 | 33KV top clamp
7130810679 | 11 kV Top Clamp Angle type 65x65x6 mm | No. | 242.99 | 11KV top clamp
7130810681 | Single Pole Cut Point Fitting 100x50 mm | Set | 2667.12 | 11KV cut point channel paint
7130810684 | D.C.Cross Arm 5.2 Mtr. Channel | No. | 6989.71 | 33 KV 4.8 MTR DC CROSS ARM
7130810692 | Stay Clamp Rail for H-Beam | Pair | 249.66 | Stay clamp for 'H' Beam
7130820008 | 11 kV Pin insulator with Pin | Each | 202 | 11KV 5KN PIN INSULATOR (POLYMER)
7130820009 | 33 kV Pin insulator with Pin | Each | 385 | 33KV 10KN PIN INSULATOR (POLYMER)
7130820010 | 11 kV Disc Insulator | Each | 142 | 11KV 45KN DISC INSULATOR T&C TYPE (POLYM
7130820011 | 33 kV Composite Disc insulator | Each | 307 | 33KV POLYMER (COMPOSITE) DISC INSULATOR
7130820018 | Split insulator | Pair | 4 | Split insulators.
7130820026 | 11 kV Post Insulator | Nos. | 428 | 11KV POST INSULATOR
7130820027 | 33 kV Post Insulator | Nos. | 1981 | 33KV POST INSULATOR
7130820029 | Cable tie for AB Cable | Each | 31
7130820030 | Disc insulator | Each | 247 | Disc Insulator
7130820071 | 11 kV Pin insulator | Each | 40 | 11 KV Pin insulator without GI Pin
7130820075 | 33 kV Pin insulator | Each | 233 | 33 KV Pin insulator without GI Pin.
7130820101 | 65 x 50 mm. | Each | 10 | SHACKEL INSULATORS: - 65 x 50 mm.
7130820106 | 90 x 75 mm. | Each | 11 | SHACKEL INSULATORS 90 x 75 mm.
7130820117 | Stay insulator | Each | 10 | Stay insulators.
7130820155 | GI Pin for 11 kV Pin insulator. | Each | 56 | GI Pin for 11 KV Pin insulator
7130820158 | GI Pin for 33 kV Pin insulator. | Each | 187 | GI Pin for 33 KV Pin insulator
7130820201 | Aluminium bobbin. | Each | 30 | Aluminium Bobbin.
7130820206 | For 65 x 50 mm insulators | Each | 28 | 7H.W. 50X65MM LT SHACKLE INSULATOR CMPLT
7130820216 | For 90 x 75 mm insulators | Each | 32 | HARDWARE FOR 75X90MM LTSHACKLE INSULATOR
7130820241 | Strain H/W up to Rabbit. | Each | 116 | 11 KV Strain hardware fittings.
7130820248 | Strain H/W for Raccoon & Dog. | Each | 241 | 33 KV Strain hardware fittings.
7130820312 | Suspension H/W suitable for Panther Conductor. | Set | 2065 | SSH ASSEMBLY WITH ARCING HORN FOR PANTHE
7130830006 | Aluminium binding wire and tape. | Kg | 130 | BINDING WIRE
7130830025 | 0.02 Sq.inch (20/22 Sqmm Al. Eq.) (Squirrel) | Km | 10485 | CONDUCTOR AAA SQURREL
7130830026 | 0.03 Sq.inch (30/34 Sqmm Al. Eq.) (Weasel) | Km | 16361 | CONDUCTOR AAA WEASEL
7130830027 | 0.05 Sq.inch (50/55 Sqmm Al. Eq.) (Rabbit) | Km | 25768 | CONDUCTOR AAA RABBIT
7130830028 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 32132 | CONDUCTOR AAA RACOON
7130830050 | Jointing sleeve for Raccoon Conductor. | Each | 30 | JOINTING SLEEVE FOR RACCOON CONDUCTOR
7130830051 | Jointing sleeve for Dog Conductor. | Each | 118 | JOINTING SLEEVE FOR DOG CONDUCTOR
7130830052 | Bimetallic clamp for Power Transformer | Each | 547
7130830053 | 0.02 Sq.inch (20 Sqmm Al. Eq.) (Squirrel) | Km | 10968 | ACSR CONDUCTOR 0.02 sqmm(20 Sqmm Al.Eq)
7130830054 | Bimetallic clamp for VCB | Each | 319
7130830055 | 0.03 Sq.inch (30 Sqmm Al. Eq.) (Weasel) | Km | 16759 | ACSR CONDUCTOR 0.03 Sqmm (30 Sqmm AlEq)
7130830056 | Bimetallic clamp for CT-PT Unit | Each | 319
7130830057 | 0.05 Sq.inch (50 Sqmm Al. Eq.) (Rabbit) | Km | 28440 | ACSR CONDUCTOR 0.05 Sqmm (50 Sqmm Al q)
7130830058 | Bimetallic clamp for Distribution Transformer (HT) | Each | 162
7130830060 | 0.075 Sq.inch (80 Sqmm Al. Eq.) (Raccoon) | Km | 42115 | ACSR CONDUCTOR 0.075 Sqmm (80 Sqmm Al.E
7130830063 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 54885 | ACSR CONDUCTOR 0.10 Sqmm (100 Sqmm lEq)
7130830070 | 0.2 Sq inch ( 130 Sqmm Al.Eq.)(Panther) | Km | 131574 | CONDUCTOR ACSR PANTHER 130 sq mm
7130830084 | 0.10 Sq.inch (100 Sqmm Al. Eq.) (Dog) | Km | 47530 | CONDUCTOR AAA DOG
7130830585 | T-Clamp for Dog Conductor. | Each | 223 | T-CLAMPS FOR ACSR CONDUCTOR Dog Conductor
7130830586 | T-Clamp for Raccoon Conductor. | Each | 178 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830586 | T-Clamp for Panther Conductor. | Each | 261 | T-CLAMPS FOR ACSR Raccoon Conductor.
7130830603 | Bimetallic clamp for Distribution Transformer (LT) | Each | 238 | Bimetallic clamps for transformer &kiosk
7130830854 | Jointing sleeves for Weasel, Squirrel & Rabbit Conductor. | Each | 24 | SLEEVE JOINTING ALUMINIUM FOR 0.03SQ INC
7130830971 | Jointing sleeves for Panther Conductor. | Each | 182 | SLEEVE REPAIR ALUMINIUM FOR .2SQ INCH AC
7130840021 | 33 kV Polymer Lightning Arrestor | Each | 3551 | LIGHTNING ARRESTORS 30 KV gapless type
7130840029 | 11 kV Polymer Lightning Arrestor | Each | 517 | LIGHTNING ARRESTORS11 KV gapless type.
7130850201 | D Transformer Mounting 100x50 mm Channel | Set | 3758.1 | Transformer mounting 100 x 50 mm channel
7130850201 | Transformer Mounting with Belting for Addl. X-Arm | No. | 3630.81 | Transformer mounting 100 x 50 mm channel
7130860017 | I-Bolt - 16 mm | No. | 98.69 | I bolt 16 mm Dia
7130860032 | Stay Set 16 mm (Painted) LT & 11 KV | Each | 345 | STAY SET WITHOUT STAY WIRE16mm Paint11KV
7130860033 | Stay Set 20 mm (Painted) | Each | 629 | STAY SET WITHOUT STAY WIRE 20mm (Painted
7130860076 | Stay Wire 7/4.00 mm (7/8 SWG) | MT | 58650 | STAY WIRES : - 7/4,00 MM (7/8 SWG).
7130860077 | Stay Wire 7/3.15 mm (7/10 SWG) | MT | 59225 | STAY WIRES: - 7/3,05 MM (7/10 SWG)
7130870010 | Earth spike | No. | 681
7130870013 | Earthing coil (Coil of 115 turns of 50 mm dia. & 2.5 Mtrs lead of 4.0 mm GI wire) | Each | 97 | EARTHING COIL 8SWG GI WIRE 50MM DIA 450M
7130870030 | Earthing Rod 25 mm 1.2 Mtr. | No. | 315.5 | Earthing rod 25 mm x 1.2 Mtrs.
7130870041 | G.I.Wire 3.15 mm (10 SWG) | MT | 53007 | G.I. WIRES: - 3,15MM (10 SWG)
7130870043 | G.I.Wire 4.0 mm (8 SWG) | MT | 52969 | G.I. WIRES: - 4,0MM (8 SWG)
7130870045 | G.I.Wire 5.0 mm (6 SWG) | MT | 52969 | G.I. WIRES: - 5,0MM (6 SWG)
7130870088 | Earthing set (Pipe earth as per DRG No.-G/008) | Each | 1812
7130870318 | Tension hardware suitable for Panther Conductor. | Set | 949 | DOUB TENS H/W FOR ZEB/ CAMEL COND S/S TY
7130877679 | Section Suspension Assembly (Suitable for all size cable) | Each | DELETED | Jointing Kit 11 kV ABC Section Suspensio
7130877681 | Dead-end Assembly (Suitable for all size cable) | Each | 2270 | Jointing kit 11 kV ABC Cable DEAD END ASM
7130877683 | Straight line Suspension Assembly (Suitable for all size cable) | Each | 2018 | Jointing Kit & HW LT ABC Cable Straight Sus
7130880006 | Cable marker for U/G cable | No. | 113 | CABLE MARKER FOR U/G CABLE
7130880006 | Pad Connector (for Panther conductor) | No. | 124 | CABLE MARKER FOR U/G CABLE
7130880041 | Danger board 33 kV & 11 kV | Each | 62 | 7130880041 Danger boards 33 kV & 11 kV.
7130890003 | M.S. sheet meter piller box | Each | DELETED | M.S. SHEET METER PILLER BOX
7130890004 | LT Feeder Piller box for 1 phase 8 connection made of M.S.Sheet. | Nos. | 3858 | LT FEEDER PILLER BOX FOR 1PH 8 CONNECTIO
7130890005 | LT Feeder Piller box for 1 phase 12 connection made of M.S.Sheet. | Nos. | 4868
7130890006 | LT Feeder Piller box for 3 phase 4 connection made of M.S.Sheet. | Nos. | 11042 | LT FEEDER PILLER BOX FOR 3PH 4 CONNECTIO
7130890007 | LT Feeder Piller box for 3 phase 8 connection made of M.S.Sheet. | Nos. | 11567 | LT FEEDER PILLER BOX FOR 3PH 8 CONNECTIO
7130890008 | L.T.Line Spacers | Nos. | 51 | LT LINE SPACERS
7131961526 | GSM Modem | Nos. | 3632 | GSM MODEM | Old Bin Code-7130890009
7130893004 | Eye Hook | No. | 161 | EYE HOOK
7130897759 | 33 kV Guarding Channel 100x50 mm | Set | 2739.85 | 33 KV guarding channel 100x50 mm.
7131210001 | Panel lndication lamps | Nos. | 106
7131210846 | Metal Halide light lamp | No. | DELETED | LAMP METAL HALIDE 250W
7131210852 | CFL 7 Watts | Each | 98
7131210881 | 250 Watt Metal Halide | Each | 1266 | METAL HALIDE LAMP 250 WATT
7131220182 | Tube Light Rod (T5 type) | Each | 52 | LAMPS: -Tube Light (40 Watts.)
7131230003 | 250 Watt Sodium Vapour | Each | 472 | 250 WATT SODIUM VAPOUR LAMP WITH HOLDER
7131230116 | 250 Watt Mercury Vapour | Each | 372 | MERCURY VAPOUR LAMP 250 WATTS 230/250 VO
7131230128 | Mercury vapour lamp for Gate lighting 2 Nos | Each | 1975 | S/ V HIGH PRESSURE LAMP 400W 230/250V
7131280006 | CFL 15 Watts | Each | 104
7131280007 | CFL 20 Watts | Each | 136 | CFL 20 WATTS LAMP
7131280008 | CFL 23 Watts | Each | 174
7131280009 | 125 Watt Mercury Vapour | Each | 161
7131280010 | Halogen Filament (1000 Watts) | Each | 100
7131280011 | Search Light Unit with 1000 Watt Halogen Lamp. | Each | 6530
7131280012 | Street Light fitting with tube light | Each | 653 | STREET LIGHT FITTING WITH TUBE LIGHT
7131280013 | Street Light fitting with CFL | Each | 2730 | STREET LIGHT FITTING WITH CFL
7131280014 | HPSV lamp 150 watt | Each | 326 | HPSV LAMP 150 WATT
7131280015 | HPSV Choke 250 watt | Each | 1360 | HPSV LAMP 250 WATT
7131280016 | 150 Watt metal halide fitting / HPSV fitting | Each | 3113 | 150 WATT METAL HALIDE HPSV FITTING
7131280017 | 250 Watt metal halide fitting / HPSV fitting | Each | 3891 | 250 WATT METAL HALIDE HPSV FITTING
7131280882 | CFL 11 Watts | Each | 98
7131300046 | Three Phase, 10-60 Amps. with poly carbonate Meter Box | Each | 2000 | ENERGY METER ENECTRONIC 10-60 AMPS
7131300065 | 3 Ø 4 Wire 0.2S accuracy class CT operated meter (for 132 kV) | Each | 1060500 | SUMMATION METER
7131300067 | Specific gravity correction chart | Nos. | 178
7131300082 | D.C.Volt meter range - 3V to + 5V | Nos. | 648 | DC VOLT METER RANG -3V TO +5V
7131300500 | Static 5.0-30 Amps Pilfer proof with transparent poly carbonate meter box. | Each | 899 | STATIC ENERGY METER S.PH 2 WIRE 5-30 A
7131300881 | CMRI | Each | 50063 | Common Meter Reading Instrument CMRI
7131310013 | 3 Ø 4 Wire 0.5S Non DLMS | Each | 3434 | HT TRIVECTOR METER 5 AMPS
7131310015 | CT operated electronic static meters with AMR (Composite Unit). | Each | 9207 | ELECTORNIC LTCT METER 3X4 100/5 A
7131310033 | 3 Ø 4 Wire 0.5S with DLMS Protocol category A | Each | 3434 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310034 | 3 Ø 4 Wire 0.5S with DLMS Protocol category B | Each | 3434 | 3PHASE 4WIRE HT TRIVECTOR STATIC (ELECTR
7131310035 | 3 Ø 3 Wire 0.2S Non DLMS | Each | 16160 | 3PHASE 4WIRE 1AMP HT TRIVECTOR STATIC (
7131310036 | 3 Ø 4 Wire 0.2S Non DLMS | Each | 16160 | 3PHASE 3WIRE 1AMP HT TRIVECTOR STATIC (
7131310037 | Test terminal Box (TTB) | Each | 870 | TTB
7131310994 | Three Phase, 20-100 Amps. with Meter Box with data storage. | Each | 2618 | LT ELEC.STATIC METER3X4X20-100A WITHLUGS | RECOMMENDED TO DELETE
7131310997 | CT operated electronic static meters 100/5 Amp. With data storage. | Each | 2027 | 3 PHASE 4 WIRE LTCT OPERATED METER
7131320009 | Digital Multimeter Electronic Type | Nos. | 2700 | MULTIMETER ELECTRONIC DIGITAL
7131321603 | Earth resistance tester (20/200/2000 Ω) | Nos. | 3940
7131324780 | Megger 500 V | Nos. | 3240
7131324806 | Megger up to 2.5 kV | Nos. | 4883 | MEGGER 1000VOLTS
7131329275 | Non Directional, 30-V, 5-Amps IDMT relay. | Each | 6300
7131334001 | Set of 3 O.C. relays instantaneous high set feature | Nos. | 7228 | SET OF 3 O.C. RELAYS INSTANTANEOUS HIGH
7131334002 | Set of 2 O.C.+ 1 earth fault relay without instantaneous high set feature | Nos. | 7286 | SET OF 2 O.C. +1 EARTH FAULT RELAY WITHO
7131399007 | Master trip relays | Nos. | 1402
7131338004 | Transil oil Dielectric Breakdown testkit | Nos. | 64638
7131338025 | Neon tester | Nos. | 51 | TESTER NEON/PENCIL/SCREW DRIVER
7131387501 | Battery Hydrometer | Nos. | 216
7131387502 | Thermometer (Wall Mounted) | Nos. | 427 | THERMOMETER (WALL MOUNTED)
7131390009 | Piercing connector suitable for 16 Sq.mm-95 Sq.mm AB Cable-Service connections | Nos. | DELETED
7131390010 | Piercing connector for Main 16-50 Sq. mm Tap off 16-50 Sq. mm. | Each | DELETED
7131390012 | Piercing connector suitable for 25 Sq.mm-95 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390013 | Piercing connector suitable for 50 Sq.mm-150 Sq.mm AB Cable-main to main connections | Nos. | DELETED
7131390014 | Earthing Coil for messenger wire | Nos. | 169
7131390015 | Anchor sleeve for messenger wire | Nos. | 31
7131390016 | Universal hook & Bolts & nuts | Nos. | 420
7131820031 | LT Single Phase MCB 5 Amps. | Each | 101
7131820032 | LT Single Phase MCB 6 to 16 Amps. | Each | 101 | 6 TO 16 AMPS LT SINGLE PHASE MCB
7131820033 | LT Three Phase MCB 16 Amps. | Each | 428
7131820034 | LT Three Phase MCB 32 Amps. | Each | 428
7131820035 | ELCB-MCB Composite Unit 10 Amps. (100 mA DP) | Each | 2853
7131820036 | ELCB-MCB Composite Unit 16 Amps. (100 mA DP) | Each | 3091
7131820037 | ELCB-MCB Composite Unit 20 Amps. (100 mA DP) | Each | 3091
7131820038 | MCCB 32 Amps. (10 kA TP) | Each | 2258
7131820039 | MCCB 160 Amps. (10 kA TP) | Each | 5171 | 160AMPS(10 KA TP) MOULDED CASE CIRCUIT B
7131900005 | Locally fabricated - 3 Phase fuse units (Robust fuse for circuit base). | Each | 694 | LT ROBUST POLE FUSE UNIT
7131900005 |  |  | 2603 | LT ROBUST POLE FUSE UNIT
7131900033 | D.O.Fuse element 11 kV (1.5 Amp. to 10 Amp.) | No. | 7 | 11KV D.O.FUSE ELEMENT (1.5 AMP TO 10 AMP
7131900071 | H.R.C. Fuse 250 Amps. | Each | 293 | HRC FUSE 250 AMPS
7131900072 | H.R.C. Fuse 400 Amps. | Each | 450 | HRC FUSE 400 AMPS
7131900625 | D.O.Fuse element 33 kV (25 Amp.) | No. | 13 | FUSE ELEMENT 25 AMPS FOR 33 KV DO
7131900650 | D.O.Fuse element 33 kV (50 Amp.) | No. | 14 | FUSE ELEMENT 50 AMPS FOR 33 KV DO
7131900876 | H.R.C. Fuse Unit 100 Amps. | Each | 289 | H.R.C. FUSE UNITS: -100 Amps.
7131900876 | H.R.C. Fuse 100 Amps. | Each | 113 | H.R.C. FUSE UNITS: -100 Amps.
7131900880 | H.R.C. Fuse Unit 250 Amps. | Each | 725 | H.R.C. FUSE UNITS: -200 Amps.
7131900881 | H.R.C. Fuse Unit 400 Amps. | Each | 802 | H.R.C. FUSE UNITS: -300 Amps.
7131900969 | T.C. Fuse Wire 22 SWG | Kg | 634 | F WIRE TINNED COPER 22 SWG24 AMP.RATING
7131900971 | T.C. Fuse Wire 20 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 20 SWG FOR 34 AM
7131900973 | T.C. Fuse Wire 18 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 18 SWG FOR 45 AM
7131900975 | T.C. Fuse Wire 16 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 16 SWG FOR 73 AM
7131900977 | T.C. Fuse Wire 14 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 14 SWG FOR 102 A
7131900979 | T.C. Fuse Wire 12 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 12 SWG
7131900981 | T.C. Fuse Wire 10 SWG | Kg | 634 | FUSE WIRE TINNED COPPER 10 SWG
7131910653 | Porcelain Kit-kat fuse unit 32 Amps. | Each | 46 | PORCELAIN KIT-KATS FUSE UNITS 32 Amps.
7131910654 | Porcelain Kit-kat fuse unit 63 Amps. | Each | 90 | PORCELAIN KIT-KATS FUSE UNITS 63 Amps.
7131910655 | Porcelain Kit-kat fuse unit 16 Amps. | Each | 26 | PORCELAIN KITKATS FUSE UNITS 16 AMPS
7131910656 | Porcelain Kit-kat fuse unit 100 Amps. | Each | 277 | PORCELAIN KIT-KATS FUSE UNITS 100 Amps.
7131910657 | Porcelain Kit-kat fuse unit 200 Amps. | Each | 550 | PORCELAIN KIT-KATS FUSE UNITS 200 Amps
7131910658 | Porcelain Kit-kat fuse unit 300 Amps. | Each | 983 | PORCELAIN KIT-KATS FUSE UNITS 300 Amps.
7131920112 | 11 kV Kiosk VCB | Each | 290958 | 12KV KIOSK TYPE OUTDOOR VACUUM CIRCUIT B
7131920253 | TPN Switches 32 Amps. | Each | 678 | TPN SWITCHES, 415 VOLTS: - 32 AMPS.
7131920254 | TPN Switches 63 Amps. | Each | 1628 | TPN SWITCHES, 415 VOLTS: - 63 AMPS. |  | 38.3421
7131920256 | TPN Switches 100 Amps. | Each | 3148 | TPN SWITCHES, 415 VOLTS: - 100 AMPS. |  | 34.043
7131920258 | TPN Switches 200 Amps. | Each | 4420 | TPN SWITCHES, 415 VOLTS: - 200 AMPS. |  | 38.7162
7131920259 | TPN Switches 300 Amps. | Each | 5997 | TPN SWITCHES, 415 VOLTS: - 300 AMPS. |  | 68.5505
7131920260 | TPN Switches 400 Amps. | Each | 9058 | TPN SWITCHES, 415 VOLTS: - 400 AMPS. |  | 51.2435
7131920767 | Distribution Board with MCB | No. | DELETED | DIST.BOARD & DP MCB 4NO 6A&2NO 16A
7131930109 | 33 kV ; 600 Amps with earth switch. | Each | 40225 | 33 KV 600AMPS WITH EARTH SWITCH ISOLATO
7131930221 | 11 kV Porcelain A.B. Switch | Each | 8675 | AB Switch with complete fitting 11 KV
7131930221 | Single phase AB switch complete. | Set | 12911 | AB Switch with complete fitting 11 KV | RECOMMENDED TO DELETE
7131930321 | 33 kV Porcelain A.B. Switch | Each | 20846 | AB SWITCH WITH COMPLETE FITTING. 33 KV
7131930412 | 11 kV Porcelain D.O. Fuse unit | Each | 1199 | DO fuse units 11KV
7131930415 | 33 kV Porcelain D.O. Fuse unit | Each | 2918 | D.O. FUSE UNITS 33 KV
7131930663 | 11 kV ; 600 Amps. | Each | 20595 | ISOLATORS COMPLETE SET11 KV; 600 Amps.
7131930752 | 33 kV ; 600 Amps without earth switch. | Each | 35641 | 33 KV Isolator 800A without earth switch
7131940602 | MCCB 100 Amps. (10 kA TP) | Each | 2378 | METER MVAR 50-0-50 32 CTR-400/1,PTR-132
7131940610 | MCCB 300 Amps. (35 kA TP) | Each | 22587 | MOULDED CASE CIRCUIT BREAKER 250/300A
7131940612 | MCCB 450 TO 500 Amps. (35 kA TP) | Each | 22587
7131941762 | 11 kV VCB without control panel & CT's. | Each | 108176 | 11 KV VCB without control panel & CT's.
7131943380 | 33 kV VCB without control panel & CT's. | Each | 223902 | 33KV VCB FOR 30 VOLT DC
7131950009 | Distribution box 1 ph. 4 connectors | Each | DELETED | DISTRIBUTION BOX 1 PH 4 CONNECTOR
7131950010 | Distribution box 1 ph. 9 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1147 | DISTRIBUTION BOX 1 PH 9 CONNECTOR
7131950011 | Distribution box 3 phase 2 connectors | Each | DELETED | DISTRIBUTION BOX 3 PH 2 CONNECTOR
7131950012 | Distribution box 3 phase 5 connectors along with 2 Nos. Steel Strap & Buckles. | Each | 1355 | DISTRIBUTION BOX 3 PH 4 CONNECTOR
7131950013 | Spring loaded distribution box for service connection with stainless steel buckle. | Each | DELETED | SPRING LOADED DIST. BOX FOR SERVICE CONN
7131950015 | L.T.Distribution Box for 500 kVA X'mer (800 A, isolator & 12 SP MCCB of 150 A) | Each | 57208
7131950016 | 11 kV Sectionalizer. | Each | 344173
7131950065 | L.T. Distribution Box for 63 kVA X'mer (200 A, isolator & 6 SP MCCB of 100 A) | Each | 13758 | DISTRIBUTION BOX FOR MCCB TYPE 63 KVA TR
7131950105 | L.T. Distribution Box for 100 kVA X'mer (200 A, isolator & 6 SP MCCB of 200 A) | Each | 17198 | DISTRIBUTION BOX FOR MSEB TYPE 100 KVA T
7131950200 | L.T. Distribution Box for 200 kVA X'mer (400 A, isolator & 6 SP MCCB of 120A) | Each | 34396 | DISTRIBUTION BOX FOR 200KVA TRANSFORMER
7131950207 | L.T. Distribution Box for 315 kVA X'mer (600 A, isolator & 9 SP MCCB of 160A) | Each | 45861 | DISTRIBUTION BOX FOR 315 KVA XMER WITH F
7131960006 | 33 kV feeder control panel (Static Relays). | Each | 26078 | 33KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960007 | 33 kV Transformer Control Panel (Static Relays) | Each | 28850 | 33KV CONTROL & RELAY PANEL- TRANSFORMER
7131960008 | Feeder Control (Static Relays) | Each | 26331 | 11KV CONTROL & RELAY PANEL- FEEDER CONTR
7131960009 | Transformer Control (Static Relays) | Each | 26995 | 11KV CONTROL & RELAY PANEL- TRANSFORMER
7131960520 | 2 Feeder Control (Static Relays) | Each | 39700 | 11KV MULTICIRCUIT(2F) CONTROL PANNELS (S
7131960522 | 1 Transformer+1 Feeder (Static Relays) | Each | 39815 | 11KV MULTICIRCUIT ONE TRANSFORMER & ONE
7131960524 | 1 Feeder + 1 Transformer (Static Relays) | Each | 39815 | 33KV MULTICIRCUIT ONE TRANSFORMER & ONE
7132002234 | Allen keys set of 9 Pcs.(1.5mm; 2mm; 2.5mm;3mm; 4mm; 5mm; 6mm; 8mm; 10mm) Black finish, box packing | Nos. | 184
7132004003 | Hack saw frames + B185 | Nos. | 119
7132004004 | Hack saw blade 300x12.5 mm | Nos. | 10
7132013331 | Discharge Rod | Nos. | 425 | FIBER GLASS DISCHARGE ROD
7132014014 | Portable drilling machine | Nos. | 2700
7132028159 | Hammer 8 Lbs (3629 gm) | Nos. | 989
7132028160 | Hammer 2 Lbs (907 gm.) | Nos. | 306
7132061858 | Combination Plier | Nos. | 204 | PLIER COMBINATION SIDE CUTTING 200 MM
7132072006 | Screw driver 250 mm | Nos. | 66 | SCREW DRIVER 250MM
7132072007 | Screw driver 200 mm | Nos. | 62 | SCREW DRIVER 200MM
7132072008 | Screw driver 150 mm | Nos. | 57 | SCREW DRIVER 150MM
7132072522 | Screw driver Set | Nos. | 743 | SCREW DRIVER INSULATED 255MM
7132074032 | Ring Spanners (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 1430 | RING SPANNER
7132074033 | Tube Spanners | Set. | 591
7132074034 | Double end spanner (6x7,8x9, 10x11,12x13,14x15,16x17,18x19, 20x22x,21x23,24x27,25x28,30x32) | Set. | 676 | DOUBLE END SPANNER
7132074035 | Adjustable Screw Spanner 12 inches | Nos. | 439
7132074036 | Box spanners (of size 32Af, 27A/F, 30 A/F& tommy Bar) | Set. | 1303 | BOX SPANNER
7132088614 | Pipe Wrench 24 inches size | Nos. | 1086
7132088615 | Pipe Wrench 18 inches size | Nos. | 596
7132200014 | 1089 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 | Each | 136101 | 11 KV CAPACITOR 600KVAR
7132200812 | 5 kVAR | Each | 1637 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200813 | 10 kVAR | Each | 3272 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200814 | 12 kVAR | Each | 3932 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200815 | 20 kVAR | Each | 6525 | POLE MOUNTED GAS FILLED LT SHUNT CAPACIT
7132200826 | 1815 kVAR 12.1 kV 3-phase 50 Hz Outdoor type Capacitor bank having step as 363 kvar+726 kvar+726 Kvar 12.1 kv Bank shall be complete with capacitor units of 121 kVAr at 6.98 kV including allied materials such as suitable size of aluminium busbars, pin/post insulators, expulsion fuses, cable jointing kit, nuts & bolts etc. | Each | 179969 | CAPACITOR BANK 11KV 3PHASE 1200 KVAR
7132210007 | 16 kVA (4 Star) Aluminium Wound | Each | 41602 | XMER 16KVA 11/0.4 FOUR STAR ALU WOUND
7132210008 | 25 kVA (4 Star) Aluminium Wound | Each | 50174 | TRANSFORMER 25KVA 11/0.4KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | 84020 | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210009 | 63 kVA (4 Star) Aluminium Wound | Each | Not Procured | TRANSFORMER 63KVA 11/0.43KV FOUR STAR
7132210010 | 100 kVA (4 Star) Aluminium Wound | Each | 116682 | TRANSFORMER 100KVA 11/0.43KV FOUR STAR
7132210011 | 200 kVA (4 Star) Aluminium Wound | Each | 204592 | TRANSFORMER 200KVA 11/0.4KV FOUR STAR
7132210012 | 315 kVA (CEA Design) | Each | 384155 | XMER 315KVA 11/0.43KV CEA REG. CU WOUND
7132210077 | 5 kVA Single Phase | Each | 25351 | TRANSFORMER 11/.4KV 5 KVA 1 PHASE | RECOMMENDED TO DELETE
7132210078 | 10 kVA Single Phase | Each | 36194 | TRANSFORMER 11/.4KV 10 KVA 1 PHASE | RECOMMENDED TO DELETE
7132210079 | 16 kVA (3 Star) Copper Wound | Each | DELETED | TRANSFORMER 11/.4KV 16 KVA 3 PHASE COPPE
7132210107 | Single Phase transformer with protection (16 kVA) | No | DELETED | Single Ph transfor with protection 16KVA
7132210108 | 25 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 25 KVA 3 STAR RATING
7132210109 | 25 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/.4 KV 25 KVA
7132210116 | 63 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 63 KVA 3 STAR RATING
7132210117 | 100 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/.4KV 100 KVA 3 STAR RATIN
7132210118 | 200 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/.4KV 200 KVA 3 STAR RATIN
7132210120 | 200 kVA (3 Star) Aluminium Wound | Each | DELETED | TRANSFORMER 11/0.4 KV 200 KVA
7132210125 | 315 kVA (Conventional) | Each | DELETED | TRANSFORMER 11/0.4 KV 315 KVA
7132210127 | 500 kVA (Conventional) | Each | 538012 | TRANSFORMER 11/0.4 KV 500 KVA | RECOMMENDED TO DELETE
7132210215 | 50 kVA (Copper winding) | Each | 133346 | TRANSFORMER 33/.4KV 50KVA
7132210231 | 63 kVA (Conventional) | Each | DELETED | TRANSFORMER 33/0.4 KV 200 KVA
7132210234 | 100 kVA (Conventional) | Each | DELETED | TRANSFORMER 33/0.4 KV 300 KVA
7132220091 | Power Transformer 1600 kVA | Each | 809678 | TRANSFORMER 33/11KV 1.6 MVA POWER
7132220095 | Power Transformer 3150 kVA | Each | 2033847 | TRANSFORMER 33/11KV 3.15 MVA POWER
7132220097 | Power Transformer 5000 kVA | Each | 2898351 | TRANSFORMER 33/11KV 5 MVA POWER
7132230015 | Indoor Type 33 kV Metering Cubical CTPT Unit 100 /5A | Each | 211216 | INDOOR TYPE 33KV CT:PT UNIT 100/5A
7132230016 | L.T.C.T. 100/5 Amps. | Each | 320 | L.T. C.T.100/5 Amps.
7132230017 | Indoor Type 33 kV Metering Cubical CTPT Unit 50/5 A | Each | 194952 | INDOOR TYPE 33KV CT:PT UNIT 50/5A
7132230019 | L.T.C.T. 200/5 Amps. | Each | 320 | L.T. C.T.200/5 Amps.
7132230021 | L.T.C.T. 300/5 Amps. | Each | 256 | L.T. C.T.300/5 Amps.
7132230024 | L.T.C.T. 500/5 Amps. | Each | 256 | L.T. C.T.500/5 Amps.
7132230039 | 220 kV C.T. 800-400/1 | No. | 517339 | 220 KV CT 800-400/1-1-1-1-1AMP.
7132230043 | 33 kV CT's (400-200/5) Amps. Oil filled | Each | 19270 | 33KV CT 400-200/5-5A
7132230065 | 132 kV C.T. 600-300/1 | No. | 330318 | CURRENT TRANSFORMER 600-300/1/1-1A,132KV
7132230075 | 132 kV C.T. 150-75/1 | No. | 377251 | 132 KV CT 150-75/1
7132230076 | 220 kV C.T. 150-75/1 | No. | 832804 | 220 KV CT 150-75/1
7132230077 | 220 kV C.T. 300-150/1 | No. | 544965 | 220 KV CT 300-150/1
7132230078 | 220 kV C.T. 600-300/1 | No. | 504120 | 220 KV CT 600-300/1
7132230088 | 11 kV CTPT Unit 400-200/5 A | Each | 31525
7132230089 | 33 kV CTPT Unit 300-150/5 A | Each | 69812 | 33KV OIL IMMERSED 3 PHASE 300-150/5A CT-
7132230185 | 11 kV C.T. 200-100/5 Amps. | Each | 9356 | 11 KV C.T's (OUT DOOR TYPE)200-100/5 A
7132230188 | 11 kV C.T. 300-150/5 Amps. | Each | 9356 | 11 KV C.T's (OUT DOOR TYPE)300-150/5 A
7132230263 | 33 kV CT's (300-150/5) Amps oil filled | Each | 20033 | 33KV CT's(300-150/5)A oil filled OD Type
7132230265 | 33 kV CT's (200-100/5) Amps oil filled | Each | 15559 | 33KV CT's(200-100/5)A oil filled OD Type
7132230304 | 33 kV CT's (100-50/5) Amps. oil filled | Each | 15260 | 33KV CT's (100-50/5)A oil filled OD Type
7132230330 | 132 kV C.T. 100-50/1 | No. | 373390 | CURRENT TRANSFORMER 100-50/1/1A SUITABLE
7132230332 | 132 kV C.T. 200-100/1 | No. | 345467 | C.T. 132KV 200-100/1/1A SUITABLE
7132230336 | 132 kV C.T. 300-150/1 | No. | 302247 | CURRENT X-MER 300-150/1/1A - 132KV
7132230394 | 11 kV CTPT Unit 7.5/5 A | Each | 36849 | OIL IMM 3 PH CTPT UNITS 11 KV 7.5/5 A
7132230395 | 11 kV CTPT Unit 10/5 A | Each | 33142 | CT/PT UNIT 11KV/110 V 10/5 A OIL IMMERSE
7132230396 | 11 kV CTPT Unit 15/5 A | Each | 33401 | OIL IMM 3 PH CTPT UNITS 11 KV 15/5 A
7132230399 | 11 kV CTPT Unit 300-150/5 A | Each | 31523 | OIL IMM 3 PH CTPT UNITS 11 KV 300-150/5A
7132230401 | 11 kV CTPT Unit 25/5 A | Each | 32154 | OIL IMM 3 PH CTPT UNITS 11 KV 25/5 A
7132230406 | 11 kV CTPT Unit 75/5 A | Each | 32154 | OIL IMM 3 PH CTPT UNITS 11 KV 75/5 A
7132230412 | 11 kV CTPT Unit 200-100/5 A | Each | 31171 | OIL IMM 3 PH CTPT UNITS 11 KV 200-100/5A
7132230414 | 11 kV CTPT Unit 50/5 A | Each | 32154 | OIL IMMERSED 3 PH CTPT UNITS-11 KV 50/5A
7132230418 | 33 kV CTPT Unit 20/5 A | Each | 67330 | OIL IMM 3 PH CTPT UNITS 33 KV - 20/5 A
7132230427 | 33 kV CTPT Unit 200-100/5 A | Each | 67142 | OIL IMM 3 PH CTPT UNITS 33 KV-200-100/5A
7132230447 | 33 kV CTPT Unit 5/5 A | Each | 80117 | OIL IMM 3 PH CTPT UNITS 33 KV - 5/5A
7132230448 | 33 kV CTPT Unit 10/5 A | Each | 67330 | OIL IMM 3 PH CTPT UNITS 33 KV - 10/5 A
7132230449 | 33 kV CTPT Unit 30/5 A | Each | 67330 | OIL IMM 3 PH CTPT UNITS 33 KV - 30/5A
7132230450 | 33 kV CTPT Unit 50/5 A | Each | 67330 | OIL IMM 3 PH CTPT UNITS 33 KV - 50/5 A
7132230453 | 33 kV CTPT Unit 100 /5A | Each | 67330 | OIL IMM 3 PH CTPT UNITS 33 KV-100&200/5A
7132230455 | 33 kV CTPT Unit 200/5A | Each | 67330 | OIL IMMERSED 3 PHASE CTPT UNITS 200/5
7132230457 | 33 kV CTPT Unit 400-200/5 A | Each | 68762 | CT/PT UNIT 33KV/110 V 400-200/5 A OIL
7132230056 | 11 kV Single Phase PT's (Oil filled) | Each | 9356 | VOLTAGE TRANSFORMER 11 K V/110 VOLTS SIN
7132230057 | 33 kV Single Phase PT's (Oil filled) | Each | 16904 | VOLTAGE TRANSFORMER 33KV/110VOLTS SINGLE
7132230501 | 132 kV P.T. | No. | 258284 | VOLTAGE TRANSFORMER 132KV/110V SINGLE PH
7132230511 | 220 kV P.T. | No. | 610018 | VOLTAGE X-MER 220KV/110-63.5V SINGLE PH
7132404015 | Safety belts | Nos. | 549 | SAFETY BELTS
7132404016 | Safety helmets | Nos. | 127 | SAFETY HELMETS
7132404366 | Battery (Low Maintenance SAN controller) | No. | 57653 | 30 Volts 100 AH lead acid battery
7132406022 | T.W. Meter Board, 300x300x75 mm, coated with varnish/SMC board | Nos. | 131 | T.W.METER BOARD, 300X300X75 MM, COATED W
7132406420 | Meter Box (GI Plain Sheet) for 3 Phase LT CT operated meter | Each | 2437 | Meter Box (GI Plain Sheet) for 3 Ph LTCT
7132406425 | Universal Meter Box for HT meters. | Each | 2553 | Universal Meter Box for HT meters.
7132406721 | CT operated electronic static meters with DLMS. | Each | 2068 | LTCT METER WITH DLMS
7132411894 | Rubber Hand gloves 15 kV (Seamless) | Pair | 455 | RUBBER HAND GLOVES
7132421002 | Fire fighting equipments CO2 fire extinguisher of 2 Kg Capacity) | No | 5166 | CO2 TYPE EXTINGUISHER ,2 KG CAPACITY
7132427634 | Rain Coats with Hoods | Nos. | 771 | RAIN COATS WITH HOODS
7132427635 | Gum Boots | Nos. | 519 | GUM BOOTS
7132438002 | Silica gel | Kg | 163 | SILICA GEL
7132444005 | Poly Carbonate seals for meter | Each | 4 | POLYCARBONATE SEAL
7132444007 | Grounding Sticks (Earthing Rods) | Set. | 893
7132448003 | Electrically insulated 11 kV mats infront of electrical control panel | No | 3696 | METTING RUBBER 1900X1800X12MM
7132455002 | T.W. plate 300x300x25 mm with 20 mm dia holes at the corners and coated with two coats of varnish on one side/SMC board | Nos. | 274
7132457798 | Transformer Oil In Barrel | KL | 51084 | TRANSFORMER OIL In Tanker/barrel
7132457798 | Transformer Oil In Tanker | KL | 43600 | TRANSFORMER OIL In Tanker/barrel
7132459005 | Poly Carbonate seal double anker type | Each | 5 | POLY CORBONATE SEAL DOUBLE ANKER TYPE
7132461004 | HDPE Pipe 200 mm ID; 240 mm OD | Mtr. | 1020 | HDPE PIPE 200MM ID; 240MM OD
7132461005 | Jointing arrangement of HDPE Pipe | Nos. | 371 | JOINTING ARRANGEMENT OF HDPE PIPE
7132468558 | Battery charger | Each | 8231 | 30 Volt 100 AH lead acid battery charger
7132475019 | Files of sizes | Set. | 310
7132475019 | Black Cambric tape 25 mm wide 7 mm thick and in rolls of 50 Mtr. | Roll | 131
7132476007 | PVC lnsulation Tapes 19 mm wide and in rolls of 10 Mtrs | Roll | 15 | PVC INSULATION TAPES 19 MM WIDE AND IN R
7132476008 | Cotton Tapes 19 mm wide and in rolls of 50 Mtrs | Roll | 71
7132478004 | Tong tester | Nos. | 1351 | DIGITAL TONG TESTER 3 1/2 DIGITAL LCD DI
7132478011 | Hand Torch 5 cell | Nos. | 534
7132478012 | Hand Torch 3 cell | Nos. | 350 | HAND TORCH 3 CELLED
7132478012 | Cotton Waste | Kg | 65 | HAND TORCH 3 CELLED
7132490006 | Fire fighting equipments (dry chemical powder type 5 Kg capacity) | No | 4619 | DRY CHEMICAL POWER FIRE
7132490052 | Monoplast | Kg | 59
7132490053 | Bitumen compound | Kg | 90
7132498006 | River sand | Cmt | 670 | RIVER SAND
ADDED IN LIST ON 20.04.2016 FOR SoR OF 2016-17
7132210015 | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer | Each | 616728 | 500 kVA [CEA Design] (4 Star) Copper Wound Transformer | NEW ITEM ADDED
7130310025 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 12056 | 16 sq.mm Single Core PVC Sheathed Unarmoured Cables
7130310026 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 18517 | 25 sq.mm Single Core PVC Sheathed Unarmoured Cables
7130310034 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 133797 | 185 sq.mm Single Core PVC Sheathed Unarmoured Cables
7130310035 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables | Km | 170583 | 300 sq.mm Single Core PVC Sheathed Unarmoured Cables
7131310168 | Spot Billing Machine | Each | 11363
11 kV Oil Immersed 3 Phase CT-PT Unit of capacity --
7132230410 | 200/5 Amp | Each | 33342 |  | NEW ITEM ADDED
7132230403 | 100/5 Amp | Each | 31629
7131960919 | 33 kV 2 feeder control panel (Static Relays) | Each | 39983
| G.I.Strip 25x3 mm | Kg | 72 |  | NEW ITEM ADDED
7132444005 | Numerical Poly Carbonate seals | No | 8
7130820011 | 33 kV Polymer Disc Insulator (45 kN) | No | 270
7130800033 | 200 Kg 8.0 Meter long PCC Pole | No | 1782
7132406420 | Pilfer proof SMC/FRPP/PPO LTCT meter box | Each | 3123

## C-1
COST SCHEDULE C-1
1 KM OF 11 kV LINE ON PCC POLE 140 KG 8.0 METER LONG WITH MAXIMUM OF 65 Mtrs SPAN USING RABBIT AND WEASEL CONDUCTOR
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 16 | 1659 | 26544 | 16 | 1659 | 26544
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 16 | 866.17 | 13858.72 | 16 | 866.17 | 13858.72
3 | Cross Arm Clamp | 7130810361 | No | 16 | 239.47 | 3831.52 | 16 | 239.47 | 3831.52
4 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 16 | 242.99 | 3887.84 | 16 | 242.99 | 3887.84
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 16 | 97 | 1552 | 16 | 97 | 1552
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 48 | 202 | 9696 | 48 | 202 | 9696
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 28.44 | 88164
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 16.759 | 51952.9
9 | Jointing sleeves suitable for 80 Sq mm. Al. Eq. ACSR Raccoon Conductor | 7130830050 | No | 6 | 30 | 180 | 6 | 30 | 180
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp | 7130810026 | No. | 4 | 120.59 | 482.36 | 4 | 120.59 | 482.36
11 | Concreting of stay @ 0.2 Cmt/stay & 0.05 Cmt base pad/pole |  | Cmt | 2 |  |  | 2
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 416 | 4.9 | 2038.4 | 416 | 4.9 | 2038.4
12 | Red Oxide Paint | 7130211158 | Ltr | 4 | 133 | 532 | 4 | 133 | 532
13 | Aluminium Paint | 7130210809 | Ltr | 4 | 297 | 1188 | 4 | 297 | 1188
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 32 | 63.963 | 2046.816 | 32 | 63.963 | 2046.816 | Earlier Qty. was 16 kG | because @2 kg per pole
15 | Danger Board | 7130880041 | Each | 16 | 62 | 992 | 16 | 62 | 992
16 | Binding wire and tape | 7130830006 | Kg | 3 | 130 | 390 | 3 | 130 | 390
17 | MS Nuts and Bolts |  | Kg | 14 |  |  | 14
| 16x90 mm | 7130620619 | Kg | 2 | 62 | 124 | 2 | 62 | 124
| 16x160 mm | 7130620627 | Kg | 16 | 61 | 976 | 16 | 61 | 976
18 | Guarding :- |  |  |  | 5956.26 |  |  | 5956.26
| (i) 11 kV Guarding Channel 100x50 mm set | 7130810511 | No | 1 | 2053.85 | 2053.85 | 1 | 2053.85 | 2053.85
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 52.969 | 1853.915 | 35 | 52.969 | 1853.915
| (iii) Stay Clamp | 7130810026 | No | 2 | 120.59 | 241.18 | 2 | 120.59 | 241.18
| (iv) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 59.225 | 651.475 | 11 | 59.225 | 651.475
| (v) Stay set 16 mm | 7130860032 | No | 2 | 345 | 690 | 2 | 345 | 690
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 116.46 | 465.84 | 4 | 116.46 | 465.84
19 | SUB TOTAL-1 |  |  |  |  | 165122.866 |  |  | 128911.766
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 14861.0579 |  | 0.09 | 11602.0589
21 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 12 | 218.6076 | 2623.2911 | 12 | 218.6076 | 2623.2911
22 | Service in lieu of concreting metal & sand only |  | Cmt | 2 | 3153.0102 | 6306.0204 | 2 | 3153.0102 | 6306.0204
23 | Labour charges as per Sch No.- CL-1 |  |  |  |  | 28980.16 |  |  | 25789.35
24 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 7192.9739 |  |  | 7192.9739
25 | SUB TOTAL-2 |  |  |  |  | 225086.3694 |  |  | 182425.4604
26 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 18163.5153 |  | 0.11 | 14180.2943
27 | Cost per Km for non-guaranteed works |  |  |  |  | 243249.8847 |  |  | 196605.7547
28 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 243250 |  |  | 196606
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.

## C-2
COST SCHEDULE C-2
11 kV DP STRUCTURE ON PCC POLE 140 KG 8 METER LONG (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | 140 Kg, 8.0 Mtr long PCC Poles | 7130800012 | No | 2 | 1659 | 3318
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 3256.41 | 3256.41
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 142 | 852
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 116 | 696
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 202 | 606
6 | Horizontal & Cross Bracing 4' Center with set of 4 back Clamps |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 33.236 | 1728.272
| (ii) Back Clamp for Pole | 7130810692 | No | 4 | 249.66 | 998.64
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 345 | 2070
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per Stay | 7130860077 | Kg | 33 | 59.225 | 1954.425
| (iii) Stay Clamp | 7130810026 | No | 6 | 120.59 | 723.54
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay |  | Cmt | 1.8
| Cement @ 208 Kg/cmt | 7130200401 | Kg | 374 | 4.9 | 1832.6
9 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 97 | 194
10 | Red Oxide paint | 7130211158 | Ltr | 0.5 | 133 | 66.5
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 297 | 148.5
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | kg | 0.5 | 63 | 31.5
| 16x200 mm | 7130620631 | kg | 5.5 | 61 | 335.5
15 | SUB TOTAL-1 |  |  |  |  | 19129.739
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 1721.6765
17 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 2 | 218.6076 | 437.2152
18 | Service in lieu of concreting metal & sand only |  | Cmt | 1.8 | 3153.0102 | 5675.4184
19 | Labour charges as per Sch. No - CL-2 |  |  |  |  | 5921.83
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 2729.7581
21 | SUB TOTAL-2 |  |  |  |  | 35615.6372
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 2104.2713
23 | Cost per DP for non-guaranteed works |  |  |  |  | 37719.9085
24 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 37720
Note: | All the rates are with considering price variation clause.

## C-3
COST SCHEDULE C-3
2016-17
1 KM OF 11 kV LINE ON H-BEAM / PCC POLE SUPPORT WITH MAXIMUM OF 80 Mtrs SPAN USING RABBIT CONDUCTOR
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 12 Nos = 4897.2 Kgs | 7130601965 | Kg | 4897.2 | 32.575 | 159526.29
2 | 365 Kg; 11 Mtr long PCC Pole |  | No |  |  |  | 12 | 4515 | 54180
3 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 866.17 | 10394.04 | 12 | 866.17 | 10394.04
4 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 12 | 249.66 | 2995.92
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 12 | 225.04 | 2700.48
5 | 11 kV Top clamp angle type with cleat | 7130810679 | No | 12 | 242.99 | 2915.88 | 12 | 242.99 | 2915.88
6 | Earthing Set (Coil earth as per Drawing No :- G/007 | 7130870013 | No | 12 | 97 | 1164 | 12 | 97 | 1164
7 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 36 | 202 | 7272 | 36 | 202 | 7272
8 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 28.44 | 88164 | 3100 | 28.44 | 88164
9 | Jointing sleeves suitable for 50 Sqmm Al Eq. ACSR Conductor | 7130830854 | No | 6 | 24 | 144 | 6 | 24 | 144
10 | (I) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380
| (II) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 59.225 | 2013.65 | 34 | 59.225 | 2013.65
(III) Stay Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 4 | 225.04 | 900.16
11 | Concreting of supports @ 0.6 Cmt. Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt. Per Stay and @ 0.05 Cmt per pole for base padding |  | Cmt. | 9 |  |  | 7.8 |  |  | Earlier concreting for PCC Pole was taken as 9 Cmt
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 1872 | 4.9 | 9172.8 | 1622.4 | 4.9 | 7949.76
12 | Red Oxide Paint | 7130211158 | Ltr | 3 | 133 | 399 | 1.7 | 133 | 226.1
13 | Aluminium Paint | 7130210809 | Ltr | 3 | 297 | 891 | 1.8 | 297 | 534.6
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 63.963 | 1535.112 | 24 | 63.963 | 1535.112 | Earlier Qty. was 12 kG | because @2 kg per pole
15 | Danger Board | 7130880041 | Each | 12 | 62 | 744 | 12 | 62 | 744
16 | Binding wire and tape | 7130830006 | Kg | 3 | 130 | 390 | 3.5 | 130 | 455
17 | MS Nuts and Bolts |  | Kg | 13 |  |  | 18
| 16x40 mm | 7130620609 | Kg | 0.5 | 63 | 31.5
| 16x65 mm | 7130620614 | Kg | 6 | 62 | 372
| 16x90 mm | 7130620619 | Kg |  |  |  | 3.5 | 62 | 217
| 16x140 mm | 7130620625 | Kg | 6.5 | 61 | 396.5
| 16x160 mm | 7130620627 | Kg |  |  |  | 14.5 | 61 | 884.5
18 | Guarding |  | LS
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2053.85 | 2053.85 | 1 | 2053.85 | 2053.85
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 52.969 | 1853.915 | 35 | 52.969 | 1853.915
| (iii) Stay Clamp | 7130810026 | No | 2 | 120.59 | 241.18 | 2 | 120.59 | 241.18
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 59.225 | 1006.825 | 17 | 59.225 | 1006.825
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 345 | 690 | 2 | 345 | 690
| (vi) I- Bolt Big Size | 7130620013 | No. | 4 | 116.46 | 465.84 | 4 | 116.46 | 465.84
19 | SUB TOTAL-1 |  |  |  |  | 297211.942 |  |  | 190085.892
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 26749.0748 |  | 0.09 | 17107.7303
21 | Service in lieu of concreting metal & sand only |  | Cmt | 9 | 3153.0102 | 28377.0918 | 9 | 3153.0102 | 28377.0918
22 | Labour charges as per Sch No - CL-4 |  |  |  |  | 40837.41 |  |  | 41948.64
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 7192.9739 |  |  | 7192.9739
24 | SUB TOTAL-2 |  |  |  |  | 400368.4925 |  |  | 284712.328
25 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 32693.3136 |  | 0.11 | 20909.4481
26 | Cost per Km for non-guaranteed works |  |  |  |  | 433061.8062 |  |  | 305621.7762
27 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 433062 |  |  | 305622
Note: - Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
All the rates are with considering price variation clause.
ITEMS REMOVED FROM Schedule- C-3 in 2016-17
1 | 60 Kg/Mtr 11.0 Mtr long Rail Pole (660 Kg each) x 12 No = 7920 Kgs | 7130601072 | Kg
5 | Back Clamp for Cross Arm
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No
11 | (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No

## C-3 (A)
COST SCHEDULE C-3 (A)
2016-17
ADDITIONAL (MID SPAN) POLES FOR 11 kV LINE
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-BEAM 152X152 MM 37.10 Kg/MTR 11.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole | 7130601965 | Kg | 408.1 | 32.575 | 13293.8575
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 866.17 | 866.17
3 | Back Clamp for Cross Arm
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 1 | 249.66 | 249.66
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 242.99 | 242.99
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 97 | 97
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 202 | 606
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding |  | Cmt. | 0.65
| Cement @ 208 Kg / Cmt | 7130200401 | Kg | 135.2 | 4.9 | 662.48
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 63.963 | 127.926 | Earlier Qty. was 1 kG | because @2 kg per pole
9 | Danger Board | 7130880041 | Each | 1 | 62 | 62
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 63 | 15.75
| 16x65 mm | 7130620614 | Kg | 0.6 | 62 | 37.2
| 16x140 mm | 7130620625 | Kg | 0.55 | 61 | 33.55
11 | SUB TOTAL-1 |  |  |  |  | 16294.5835
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 1466.5125
13 | Service in lieu of concreting metal & sand only |  | Cmt | 0.65 | 3153.0102 | 2049.4566
14 | Labour charges as per Sch No. CL-4 (revised based on one pole) |  |  |  |  | 1988.4772
15 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 359.6487
16 | SUB TOTAL-2 |  |  |  |  | 22158.6785
17 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 1792.4042
18 | Cost per pole for non-guaranteed works |  |  |  |  | 23951.0827
19 | Cost per Pole (Rounded off) |  |  |  |  | 23951

## C-3 (B)
COST SCHEDULE C-3 (B)
COST PER KM OF 11 kV LINE ON AERIAL BUNCHED CABLE (ABC) OF 35 & 70 SQ.MM. ON 11 MTR. LONG H - BEAM / 9.0 MTR LONG PCC POLE OF SPAN 35 MTRS.
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | "H" Beam 152x152mm 37.1 Kg/Mtr 11.0 Mtr long |  |  |  | 200 Kg; 9.0 Mtr long PCC Pole
[5 empty] | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm |  | Using 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm
[5 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 29 Nos = 11835 Kgs | 7130601965 | Kg | 32.575 | 11835 | 385525.125 | 11835 | 385525.125
2 | 200 Kg 9.0 Meter long PCC Pole |  | No. | 2195 |  |  |  |  | 29 | 63655 | 29 | 63655
3 | 11 kV 3 phase Aerial Bunched Cable 3x35+35 sqmm (incl. 6% sag) | 7130310057 | Km | 281789 | 1.06 | 298696.34 |  |  | 1.06 | 298696.34
4 | 11 kV 3 phase Aerial Bunched Cable 3x70+70 sqmm (incl. 6% sag) | 7130310058 | Km | 398660 |  |  | 1.06 | 422579.6 |  |  | 1.06 | 422579.6
5 | 11 kV Termination kit 35-70 sqmm | 7130320048 | Set | 2396 | 9 | 21564 | 9 | 21564 | 9 | 21564 | 9 | 21564
6 | 11 kV AB Cable straight through jointing kit suitable for 35-70 sqmm | 7130310061 | Set | 3784 | 6 | 22704 | 6 | 22704 | 6 | 22704 | 6 | 22704
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2270 | 16 | 36320 | 16 | 36320 | 16 | 36320 | 16 | 36320
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 2018 | 21 | 42378 | 21 | 42378 | 21 | 42378 | 21 | 42378
9 | Eye Hook | 7130893004 | No. | 161 | 40 | 6440 | 40 | 6440 | 40 | 6440 | 40 | 6440
10 | Stay set 16 mm | 7130860032 | No. | 345 | 12 | 4140 | 12 | 4140 | 12 | 4140 | 12 | 4140
11 | Stay wire 7/10 SWG 10 kg/stay | 7130860077 | Kg | 59.225 | 120 | 7107 | 120 | 7107 | 120 | 7107 | 120 | 7107
12 | Earth spike | 7130870010 | No. | 681 | 29 | 19749 | 29 | 19749 | 29 | 19749 | 29 | 19749
13 | G.I. Wire 6 SWG | 7130870045 | Kg | 52.969 | 24 | 1271.256 | 24 | 1271.256 | 24 | 1271.256 | 24 | 1271.256
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 63.963 | 58 | 3709.854 | 58 | 3709.854 | 58 | 3709.854 | 58 | 3709.854 | Earlier Qty. was 29 kG | because @2 kg per pole
15 | Pole Clamp | 7130810077 | No. | 394 | 37 | 14578 | 37 | 14578 | 37 | 14578 | 37 | 14578
16 | Danger Board | 7130880041 | Each | 62 | 29 | 1798 | 29 | 1798 | 29 | 1798 | 29 | 1798
17 | Pad Connector | 7130880006 | No. | 124 | 3 | 372 | 3 | 372 | 3 | 372 | 3 | 372
18 | Concreting of Pole @ 0.65 Cmt per pole and 0.2 Cmt per stay |  | Cmt. |  | 21.25 |  | 21.25 |  | 2.4 |  | 2.4
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 4420 | 21658 | 4420 | 21658
19 | Red Oxide Paint | 7130211158 | Ltr | 133 | 8 | 1064 | 8 | 1064
20 | Aluminium Paint | 7130210809 | Ltr | 297 | 8 | 2376 | 8 | 2376
21 | M.S.Nuts and Bolts |  | Kg |  | 30 |  | 30 |  | 30 |  | 30
| 16x40 mm | 7130620609 | Kg | 63 | 12 | 756 | 12 | 756 | 12 | 756 | 12 | 756
| 16x65 mm | 7130620614 | Kg | 62 | 12 | 744 | 12 | 744 | 12 | 744 | 12 | 744
| 16x140 mm | 7130620625 | Kg | 61 | 6 | 366 | 6 | 366 | 6 | 366 | 6 | 366
22 | Cable tie (UV protected black colour) for AB Cable (at every two meter) | 7130820029 | No. | 31 | 530 | 16430 | 530 | 16430 | 530 | 16430 | 530 | 16430 | Earlier Bin Code - 7130320053
23 | SUB TOTAL-1 |  |  |  |  | 909746.575 |  | 1033629.835 |  | 562778.45 |  | 686661.71
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 81877.1917 | 0.09 | 93026.6852 | 0.09 | 50650.0605 | 0.09 | 61799.5539
25 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No. | 218.6076 |  |  |  |  | 29 | 6339.6202 | 29 | 6339.6202
26 | Service in lieu of concreting metal & sand only |  | Cmt | 3153.0102 | 21.25 | 67001.4668 | 21.25 | 67001.4668
27 | Labour charges as per Sch No. CL-3(B) |  |  |  |  | 123615.53 |  | 123615.53 |  | 111163.32 |  | 111163.32
28 | Transportation charges |  |  |  |  | 17982.1682 |  | 17982.1682 |  | 17982.1682 |  | 17982.1682
29 | SUB TOTAL-2 |  |  |  |  | 1200222.9317 |  | 1335255.6851 |  | 748913.6189 |  | 883946.3723
30 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 100072.1233 |  | 113699.2818 |  | 61905.6295 |  | 75532.7881
31 | Total Cost per Km including labour charges |  |  |  |  | 1300295.055 |  | 1448954.967 |  | 810819.2484 |  | 959479.1604
32 | Total Cost (Round off) |  |  |  |  | 1300295 |  | 1448955 |  | 810819 |  | 959479

## C-3 (C)
COST SCHEDULE C-3 (C)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RACCOON CONDUCTOR
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | Raccoon Conductor | 7130830060 | Km | 3.03 | 42115 | 127608.45
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2053.85 | 2053.85
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 52.969 | 1853.915
4 | Stay Clamp | 7130810026 | No | 2 | 120.59 | 241.18
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 59.225 | 651.475
6 | Stay set 16 mm | 7130860032 | No | 2 | 345 | 690
7 | I-Bolt Big size | 7130620013 | No | 4 | 116.46 | 465.84
8 | Material Cost |  |  |  |  | 133564.71
9 | Dismantling Charges |  | Ckt Km | 1 | 4160.985 | 4160.985
10 | Stringing Charges as per Labour Rate Schedule AL-1 |  | Ckt Km | 1 | 8321.97 | 8321.97
11 | SUB TOTAL-1 |  |  |  |  | 146047.665
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 13144.2898
13 | Transportation charges |  |  |  |  | 2740.6827
14 | SUB TOTAL-2 |  |  |  |  | 161932.6376
15 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 16065.2432
16 | Cost per Km |  |  |  |  | 177997.8807
17 | Total Cost (Round off) |  |  |  |  | 177998

## C-3 (D)
COST SCHEDULE C-3 (D)
SCHEDULE FOR AUGMENTATION OF 1 kM OF 11 kV LINE FROM WEASEL TO RABBIT CONDUCTOR
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty | Rate | Amount
1 | Rabbit Conductor | 7130830057 | Km | 3.03 | 28440 | 86173.2
2 | 11 kV Guarding Channel 100x50 mm set. | 7130810511 | No | 1 | 2053.85 | 2053.85
3 | G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 52.969 | 1853.915
4 | Stay Clamp | 7130810026 | No | 2 | 120.59 | 241.18
5 | Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 11 | 59.225 | 651.475
6 | Stay set 16 mm | 7130860032 | No | 2 | 345 | 690
7 | I-Bolt Big size | 7130620013 | No. | 4 | 116.46 | 465.84
8 | Material Cost |  |  |  |  | 92129.46
9 | Dismantling Charges |  | Ckt Km | 1 | 3850.9 | 3850.9
10 | Stringing Charges as per Labour Rate Schedule CL-1 |  | Ckt Km | 1 | 7701.8 | 7701.8
11 | SUB TOTAL-1 |  |  |  |  | 103682.16
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 9331.3944
13 | Transportation charges |  |  |  |  | 2740.6827
14 | SUB TOTAL-2 |  |  |  |  | 115754.2371
15 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 11405.0376
16 | Cost per Km |  |  |  |  | 127159.2747
17 | Total Cost (Round off) |  |  |  |  | 127159

## C-3 (E)
COST SCHEDULE C-3 (E)
2016-17
COST PER KM OF 11 kV OVERHEAD XLPE CABLE LINE ON H - BEAM POLE WITH AVERAGE SPAN 30 MTRS.
Assumed as if cable length is 500 Mtr. in one stroke.
S. No. | PARTICULARS | New SAP Bin Code | Unit | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 33 Nos = 13467.3 Kgs | 7130601965 | Kg | 13467.3 | 32.575 | 438697.2975
2 | 11 kV XLPE 3 Core Cable 120 sqmm (incl. sag 6%) | 7130310078 | Mtr. | 1060 | 761.409 | 807093.54
3 | 11 kV End Termination kit for XLPE Cable 150 sqmm | 7130352040 | Set | 42 | 10187 | 427854
4 | 11 kV Straight thru' joint kit suitable for 120 sqmm Cable | 7130310062 | Set | 4 | 3982 | 15928
5 | Earth spike | 7130870010 | No. | 6 | 681 | 4086
6 | D.C.Cross Arm 5.2 Mtr. Channel | 7130810684 | Set | 2 | 6989.71 | 13979.42
7 | Dead-end Assembly (Suitable for all size cable) | 7130877681 | No. | 2 | 2270 | 4540 | Earlier Bin Code -7130797532
8 | Straight line Suspension Assembly (Suitable for all size cable) | 7130877683 | No. | 31 | 2018 | 62558 | Earlier Bin Code - 7130797533
9 | Eye Hook | 7130893004 | No. | 33 | 161 | 5313
10 | Stay set without stay wire 20 mm | 7130860033 | No. | 12 | 629 | 7548
11 | Stay wire 7/8 SWG 10 kg/stay | 7130860076 | Kg | 120 | 58.65 | 7038
12 | Stay clamp for H-Beam | 7130810692 | No. | 24 | 249.66 | 5991.84
13 | Clamp for H-Beam | 7130810692 | No. | 33 | 249.66 | 8238.78
14 | M.S.Angle 65x65x6 mm | 7130600032 | Kg | 330 | 33.236 | 10967.88
15 | Red Oxide Paint | 7130211158 | Ltr | 3 | 133 | 399
16 | Aluminium Paint | 7130210809 | Ltr | 3 | 297 | 891
17 | Earthing Coil | 7130870013 | No. | 33 | 97 | 3201
18 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 66 | 63.963 | 4221.558 | Earlier Qty. was 33 kG | because @2 kg per pole
19 | Danger Board | 7130880041 | No. | 33 | 62 | 2046
20 | Concreting of Pole @ 0.65 Cmt per pole and 0.3 Cmt per stay |  | Cmt | 25.05
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 5210.4 | 4.9 | 25530.96
21 | M.S.Nuts and Bolts |  | Kg | 40
| 16x65 mm | 7130620614 | Kg | 26 | 62 | 1612
| 16x200 mm | 7130620631 | Kg | 14 | 61 | 854
22 | SUB TOTAL-1 |  |  |  |  | 1858589.2755
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 167273.0348
24 | Labour charges 7% of material cost |  |  |  |  | 178230.5067
25 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) | 3% of material cost |  |  |  | 61125.6418
26 | Service in lieu of Concreting |  | Cmt | 21.45 | 3153.0102 | 67632.0688
27 | Service in lieu of Earthing Coal & Salt etc |  | No. | 33 | 1942.2007 | 64092.6228
28 | SUB TOTAL-2 |  |  |  |  | 2396943.1504
29 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 204444.8203
30 | Total Cost per Km including labour charges |  |  |  |  | 2601387.9707
31 | Total Cost (Round off) |  |  |  |  | 2601388

## C-4
COST SCHEDULE C-4
11 kV DP STRUCTURE ON H-BEAM / PCC POLE SUPPORT (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long |  |  | 365 Kg 11 Mtr long PCC Pole
|  |  |  | Qty | Rate | Amount | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 32.575 | 26587.715
2 | 365 Kg; 11 Mtr long PCC Pole |  | No |  |  |  | 2 | 4515 | 9030
3 | DC Cross Arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | No | 1 | 3256.41 | 3256.41 | 1 | 3256.41 | 3256.41
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 142 | 852 | 6 | 142 | 852
5 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 116 | 696 | 6 | 116 | 696
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 202 | 606 | 3 | 202 | 606
7 | Horizontal & Cross Bracing 4' center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 33.236 | 1728.272 | 52 | 33.236 | 1728.272
Back Clamp for Pole
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 4 | 225.04 | 900.16
8 | (I) Stay set 16 mm | 7130860032 | No | 6 | 345 | 2070 | 6 | 345 | 2070
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 59.225 | 3020.475 | 51 | 59.225 | 3020.475
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 6 | 249.66 | 1497.96
| (ii) Stay Clamp for PCC Pole | 7130810193 | No |  |  |  | 6 | 225.04 | 1350.24
9 | Concreting of pole @ 0.6 Cmt Per Pole for H-Beam ; @ 0.5 Cmt. Per pole for 365 kG PCC & @ 0.2 Cmt per stay and @ 0.05 Cmt per pole for base padding |  | Cmt | 2.5 |  |  | 2.3 |  |  | Earlier concreting for PCC Pole was taken as 2.5 Cmt
| Cement @ 208 Kg/cmt | 7130200401 | Kg | 520 | 4.9 | 2548 | 478.4 | 4.9 | 2344.16
10 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 97 | 194 | 2 | 97 | 194
11 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 133 | 66.5 | 0.5 | 133 | 66.5
12 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 297 | 148.5 | 0.5 | 297 | 148.5
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
14 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62
15 | MS Nuts and Bolts |  | Kg | 6 |  |  | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 63 | 31.5 | 0.5 | 63 | 31.5
| 16x200 mm | 7130620631 | Kg | 5.5 | 61 | 335.5 | 5.5 | 61 | 335.5
16 | SUB TOTAL-1 |  |  |  |  | 44955.324 |  |  | 26947.569
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 4045.9792 |  | 0.09 | 2425.2812
18 | Service in lieu of concreting metal & sand only |  | Cmt | 2.5 | 3153.0102 | 7882.5255 | 2.5 | 3153.0102 | 7882.5255
19 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 7421.49 |  |  | 7598.12
20 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 2729.7581 |  |  | 2729.7581
21 | SUB TOTAL-2 |  |  |  |  | 67035.0768 |  |  | 47583.2538
22 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 4945.0856 |  | 0.11 | 2964.2326
23 | Cost per DP for non-guaranteed works |  |  |  |  | 71980.1624 |  |  | 50547.4864
24 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 71980 |  |  | 50547
Note: | All the rates are with considering price variation clause.
ITEMS REMOVED FROM Schedule- C-4 in 2016-17
1 | 60 Kg/Mtr 11.0 Mtr long Rail Pole (660 Kg each) x 2 No = 1320 Kgs | 7130601072 | Kg
2 | Horizontal & Cross Bracing 4' center with set of 4 back clamp |  | Set
Back Clamp for Pole
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No
3 | (III) Stay Clamp
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No

## C-5
COST SCHEDULE C-5
1 kM OF 11 kV LINE ON 175x85 MM R.S. JOIST WITH MAXIMUM OF 65 Mtrs. SPAN USING RABBIT AND WEASEL CONDUCTOR
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Using RABBIT Conductor |  |  | Using WEASEL Conductor
|  |  |  | Qnty | Rate | Amount | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
1 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 Mtr = 214.44 kg x 12 No = 2573.28 Kgs | 7130600675 | Kg | 2573 | 32.575 | 83815.475 | 2573 | 32.575 | 83815.475
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 12 | 866.17 | 10394.04 | 12 | 866.17 | 10394.04
3 | Back Clamp for Cross Arm | 7130810361 | No | 12 | 239.47 | 2873.64 | 12 | 239.47 | 2873.64
4 | 11 kV Top clamp Angle type with cleat | 7130810679 | No | 12 | 242.99 | 2915.88 | 12 | 242.99 | 2915.88
5 | Earthing Set (Coil earth as per Drawing No:-G/007) | 7130870013 | No | 12 | 97 | 1164 | 12 | 97 | 1164
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 36 | 202 | 7272 | 36 | 202 | 7272
7 | ACSR conductor RABBIT with 3% sag | 7130830057 | Mtr | 3100 | 28.44 | 88164
8 | ACSR conductor Weasel with 3% sag | 7130830055 | Mtr |  |  |  | 3100 | 16.759 | 51952.9
9 | Jointing sleeves suitable for 80 Sq.mm. Al Eq. ACSR Conductor | 7130830050 | No | 6 | 30 | 180 | 6 | 30 | 180
10 | (i) Stay set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 34 | 59.225 | 2013.65 | 34 | 59.225 | 2013.65
| (iii) Stay Clamp for R.S. Joist | 7130810216 | No. | 4 | 239.47 | 957.88 | 4 | 239.47 | 957.88
11 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 cmt/pole |  | Cmt | 5.4 |  |  | 5.4 |  |  | Earlier concreting for R.S. Joist was taken as 5 Cmt
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 1123.2 | 4.9 | 5503.68 | 1123.2 | 4.9 | 5503.68
12 | Red Oxide Paint | 7130211158 | Ltr | 2.5 | 133 | 332.5 | 2.5 | 133 | 332.5
13 | Aluminium Paint | 7130210809 | Ltr | 2.5 | 297 | 742.5 | 2.5 | 297 | 742.5
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 24 | 63.963 | 1535.112 | 24 | 63.963 | 1535.112 | Earlier Qty. was 12 kG | because @2 kg per pole
15 | Danger Board | 7130880041 | Each | 12 | 62 | 744 | 12 | 62 | 744
16 | Binding wire and tape | 7130830006 | Kg | 3 | 130 | 390 | 3 | 130 | 390
17 | MS Nuts and Bolts |  | Kg | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 5 | 63 | 315 | 5 | 63 | 315
| 16x65 mm | 7130620614 | Kg | 4 | 62 | 248 | 4 | 62 | 248
| 16x90 mm | 7130620619 | Kg | 5 | 62 | 310 | 5 | 62 | 310
18 | Guarding :-
| (i) 11 kV Guarding Channel 100x50 mm | 7130810511 | No | 1 | 2053.85 | 2053.85 | 1 | 2053.85 | 2053.85
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 35 | 52.969 | 1853.915 | 35 | 52.969 | 1853.915
| (iii) Stay Clamp | 7130810026 | No | 2 | 120.59 | 241.18 | 2 | 120.59 | 241.18
| (iv) Stay Wire 7/10 SWG @ 8.5 Kg/Stay | 7130860077 | Kg | 17 | 59.225 | 1006.825 | 17 | 59.225 | 1006.825
| (v) Stay set 16 mm with turn buckle without stay wire | 7130860032 | No | 2 | 345 | 690 | 2 | 345 | 690
| (vi) I- Bolt Big size | 7130620013 | No | 4 | 116.46 | 465.84 | 4 | 116.46 | 465.84
19 | SUB TOTAL-1 |  |  |  |  | 217562.967 |  |  | 181351.867
20 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 19580.667 |  | 0.09 | 16321.668
21 | Service in lieu of concreting metal & sand only |  | Cmt | 5 | 3153.0102 | 15765.051 | 5 | 3153.0102 | 15765.051
22 | Labour charges as per Sch. No. CL-6 |  |  |  |  | 40837.41 |  |  | 40197.26
23 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 7192.9739 |  |  | 7192.9739
24 | SUB TOTAL-2 |  |  |  |  | 300939.069 |  |  | 260828.82
25 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 23931.9264 |  | 0.11 | 19948.7054
26 | Cost per Km for non-guaranteed works |  |  |  |  | 324870.9953 |  |  | 280777.5253
27 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 324871 |  |  | 280778
Note: - (1) Schedule C-2 is to be supplemented with every 1.0 Km. 11 kV line.
(2) All the rates are with considering price variation clause.
ITEMS REMOVED FROM Schedule- C-5 in 2016-17
| 11 kV G.I. Pin | 7130820155 | No

## C-6
2016-17
COST SCHEDULE C-6
11 kV DP STRUCTURE ON 175X85 MM R.S. JOIST (TO BE SUPPLEMENTED WITH EVERY 1.0 Kms OF LINE)
Sl. No. | PARTICULARS | New SAP Bin Code | Unit | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | R.S. Joist (175x85 mm) 11 Mtr Long i.e. 214.44 Kg/pole @ 19.495 Kg/Mtr. i.e.214.44x2 No pole=428.89 Kgs | 7130600675 | Kg | 428.89 | 32.575 | 13971.0917
2 | DC Cross arm of 100x50 mm channel (4'/1.2 Mtr. Centre) | 7130810512 | Set | 1 | 3256.41 | 3256.41
3 | 11 kV Polymer Disc Insulator | 7130820010 | No. | 6 | 142 | 852
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 116 | 696
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 202 | 606
6 | Horizontal & Cross Bracing 4' Center with set of 4 back clamp |  | Set
| (i) M.S.Angle 65x65x6 mm | 7130600032 | Kg | 52 | 33.236 | 1728.272
| (ii) Back Clamp for Pole | 7130810216 | No | 4 | 239.47 | 957.88
7 | (i) Stay set 16 mm | 7130860032 | No | 6 | 345 | 2070
| (ii) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 51 | 59.225 | 3020.475
| (iii) Stay Clamp for R.S. Joist | 7130810216 | No | 6 | 239.47 | 1436.82
8 | Concreting of pole @ 0.3 Cmt and 0.2 Cmt per stay & pole base padding @ 0.05 Cmt/pole |  | Cmt | 1.9
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 395 | 4.9 | 1935.5
9 | Earthing Set (Coil earth as per Drawing No - G/007) | 7130870013 | No | 1 | 97 | 97
10 | Red Oxide Paint | 7130211158 | Ltr | 0.5 | 133 | 66.5
11 | Aluminium Paint | 7130210809 | Ltr | 0.5 | 297 | 148.5
12 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62
14 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 63 | 31.5
| 16x65 mm | 7130620614 | Kg | 2.5 | 62 | 155
| 16x200 mm | 7130620631 | Kg | 3 | 61 | 183
15 | SUB TOTAL-1 |  |  |  |  | 31529.8007
16 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 2837.6821
17 | Service in lieu of concreting metal & sand only |  | Cmt | 1.9 | 3153.0102 | 5990.7194
18 | Labour charges as per Sch. No. CL-7 |  |  |  |  | 7421.49
19 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 2729.7581
20 | SUB TOTAL-2 |  |  |  |  | 50509.4503
21 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 3468.2781
22 | Cost per DP for non-guaranteed works |  |  |  |  | 53977.7284
23 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 53978
Note: | All the rates are with considering price variation clause.

## C-7(A-1)
COST SCHEDULE C-7 (A-1)
2016-17
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED R.S. JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND 3.5 CORE PVC INSULATED CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Conventional)
| (i) 25 kVA TRANSFORMER (4 STAR) | 7132210008 | Each | 1 | 50174 | 50174
| (ii) 63 kVA TRANSFORMER (4 STAR) | 7132210009 | Each |  |  |  | 1 | 84020 | 84020
| (iii) 100 kVA TRANSFORMER (4 STAR) | 7132210010 | Each | [6 empty] | 1 | 116682 | 116682
| (iv) 200 kVA TRANSFORMER (4 STAR) | 7132210011 | Each | [9 empty] | 1 | 204592 | 204592
2 | (i) 140 Kg 8.0 Mtr long PCC Pole | 7130800012 | No | 3 | 1659 | 4977 | 3 | 1659 | 4977 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 32.575 | 27942.1835 | 857.78 | 32.575 | 27942.1835
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426
| 11 kV H.W. | 7130820241 | No. | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597
8 | M.S. Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp | 7130810026 | No | 4 | 120.59 | 482.36 | 4 | 120.59 | 482.36 | 4 | 120.59 | 482.36
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole |  | Cmt | 1.85 |  |  | 1.85 |  |  | 1.85 |  |  | 1.85
| (i) Cement @ 208 Kg/cmt | 7130200401 | Kg | 384.8 | 4.9 | 1885.52 | 384.8 | 4.9 | 1885.52 | 395.2 | 4.9 | 1936.48 | 395.2 | 4.9 | 1936.48
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 63.963 | 383.778 | 6 | 63.963 | 383.778 | 8 | 63.963 | 511.704 | 8 | 63.963 | 511.704 | Earlier Qty. was 2 kG | because @2 kg per pole
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133 | 1 | 133 | 133 | 3 | 133 | 399 | 3 | 133 | 399
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297 | 1 | 297 | 297 | 3 | 297 | 891 | 3 | 297 | 891
18 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63
| 16x65 mm | 7130620614 | Kg | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248
| 16x140 mm | 7130620625 | Kg | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244
| 16x200 mm | 7130620631 | Kg | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1628 | 1628 | -- |  |  | -- |  |  | --
21 | PVC insulated 4 Core cable
i | 16 Sqmm (Armoured) | 7130311084 | Mtr | 30 | 52.156 | 1564.68 | -- | [5 empty] | --
ii | 70 Sqmm | 7130311054 | Mtr | -- | -- | -- | 30 | 114.082 | 3422.46 | 30 | 114.082 | 3422.46 | -- | -- | --
iii | 150 Sqmm | 7130311057 | Mtr | -- | -- | -- | -- | -- | -- | 10 | 394.64 | 3946.4 | 30 | 394.64 | 11839.2
iv | 300 Sqmm | 7130311061 | Mtr | -- | -- | -- | -- | -- | -- | -- | -- | -- | 10 | 626.228 | 6262.28
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 13758 | 13758 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 17198 | 17198
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 34396 | 34396
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8675 | 8675 | 1 | 8675 | 8675
24 | SUB TOTAL-1 |  |  |  |  | 86726.397 |  |  | 134560.177 |  |  | 207287.6465 |  |  | 322645.9065
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 7805.3757 |  | 0.09 | 12110.4159 |  | 0.09 | 18655.8882 |  | 0.09 | 29038.1316
26 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 218.6076 | 655.8228 | 3 | 218.6076 | 655.8228 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 192.6179
27 | Service in lieu of concreting metal & sand only |  | Cmt | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689
28 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
29 | Labour charges as per Sch CL-3 |  |  |  |  | 8460.67 |  |  | 8887.44 |  |  | 8887.44 |  |  | 11027.94
30 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  |  |  | 4137.5359 |  |  | 4580.5306 |  |  | 4580.5306 |  |  | 4580.5306
31 | SUB TOTAL-2 |  |  |  |  | 119445.4967 |  |  | 172454.0816 |  |  | 251071.2006 |  |  | 378952.204
32 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 9539.9037 |  | 0.11 | 14801.6195 |  | 0.11 | 22801.6411 |  | 0.11 | 35491.0497
33 | Cost per S/s for non-guaranteed works |  |  |  |  | 128985.4004 |  |  | 187255.7011 |  |  | 273872.8417 |  |  | 414443.2537
34 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 128985 |  |  | 187256 |  |  | 273873 |  |  | 414443
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist 175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.

## C-7(A-2)
COST SCHEDULE C-7 (A-2)
2016-17
11/0.4 kV OUT DOOR SUB-STATION (USING PCC POLE FOR 25/63 kVA TRANSFORMER & DOUBLE WELDED RS JOIST 175x85 mm FOR 100/200 kVA TRANSFORMER AND SINGLE CORE CABLE)
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Conventional)
| (i) 25 kVA TRANSFORMER (4 STAR) | 7132210008 | Each | 1 | 50174 | 50174
| (ii) 63 kVA TRANSFORMER (4 STAR) | 7132210009 | Each |  |  |  | 1 | 84020 | 84020
| (iii) 100 kVA TRANSFORMER (4 STAR) | 7132210010 | Each | [6 empty] | 1 | 116682 | 116682
| (iv) 200 kVA TRANSFORMER (4 STAR) | 7132210011 | Each | [9 empty] | 1 | 204592 | 204592
2 | (i) 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 1659 | 4977 | 3 | 1659 | 4977 | -- | -- | -- | -- | -- | --
| (ii) 175x85 mm 11.0 Mtr long R.S. Joist @ 19.495 Kg/mtr x 9 mtr = 175.45 kg/pole x 2 No = 428.9 Kgs, For 4 No pole = 857.8 Kg | 7130600675 | Kg | [6 empty] | 857.78 | 32.575 | 27942.1835 | 857.78 | 32.575 | 27942.1835
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426
5 | 11 kV H.W | 7130820241 | No | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212
7 | 11 kV DO fuse & LA mounting DC cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63
8 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597
9 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72
10 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp | 7130810026 | No | 4 | 120.59 | 482.36 | 4 | 120.59 | 482.36 | 4 | 120.59 | 482.36
11 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole |  | Cmt | 1.85 |  |  | 1.85 |  |  | 1.85 |  |  | 1.85
| (i) Cement @ 208 Kg/cmt | 7130200401 | Kg | 385 | 4.9 | 1886.5 | 385 | 4.9 | 1886.5 | 312 | 4.9 | 1528.8 | 312 | 4.9 | 1528.8
12 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024
13 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
14 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62
15 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
16 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 63.963 | 383.778 | 6 | 63.963 | 383.778 | 8 | 63.963 | 511.704 | 8 | 63.963 | 511.704 | Earlier Qty. was 2 kG | because @2 kg per pole
17 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133 | 1 | 133 | 133 | 3 | 133 | 399 | 3 | 133 | 399
18 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297 | 1 | 297 | 297 | 3 | 297 | 891 | 3 | 297 | 891
19 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551
20 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63
| 16x65 mm | 7130620614 | Kg | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248
| 16x140 mm | 7130620625 | Kg | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244
| 16x200 mm | 7130620631 | Kg | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305
21 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1628 | 1628 | -- |  |  | -- |  |  | --
22 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.819 | 1778.28 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr |  |  |  | 80 | 24.976 | 1998.08
iii | 50 Sqmm | 7130311009 | Mtr |  |  |  | 40 | 34.517 | 1380.68 | 120 | 34.517 | 4142.04
iv | 70 Sqmm | 7130311010 | Mtr | -- | [5 empty] | 40 | 46.364 | 1854.56 | 120 | 46.364 | 5563.68
v | 150 Sqmm | 7130311011 | Mtr | -- | [8 empty] | 40 | 87.502 | 3500.08
23 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 13758 | 13758 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 17198 | 17198
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 34396 | 34396
24 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8675 | 8675 | 1 | 8675 | 8675
25 | SUB TOTAL-1 |  |  |  |  | 86940.977 |  |  | 134517.457 |  |  | 205507.7065 |  |  | 313200.5065
26 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 7824.6879 |  | 0.09 | 12106.5711 |  | 0.09 | 18495.6936 |  | 0.09 | 28188.0456
27 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 218.6076 | 655.8228 | 3 | 218.6076 | 655.8228 | 0 | 0 | 0 | 0 | 0 | 0
28 | Service in lieu of concreting metal & sand only |  | Cmt | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689 | 1.85 | 3153.0102 | 5833.0689
29 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
30 | Labour charges as per Sch. CL-3 |  |  |  |  | 8460.67 |  |  | 8887.44 |  |  | 8887.44 |  |  | 11027.94
31 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 4137.5359 |  |  | 4580.5306 |  |  | 4580.5306 |  |  | 4580.5306
32 | SUB TOTAL-2 |  |  |  |  | 119679.3889 |  |  | 172407.5168 |  |  | 249131.066 |  |  | 368656.718
33 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 9563.5075 |  | 0.11 | 14796.9203 |  | 0.11 | 22605.8477 |  | 0.11 | 34452.0557
34 | Cost per S/s for non-guaranteed works |  |  |  |  | 129242.8964 |  |  | 187204.4371 |  |  | 271736.9137 |  |  | 403108.7737
35 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 129243 |  |  | 187204 |  |  | 271737 |  |  | 403109
Note (A) :- (1) All the rates are with considering price variation clause.
(2) Single RS Joist175x85 mm may be used in place of PCC pole for 25/63 kVA Transformer
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## C-7(B-1)
COST SCHEDULE C-7 (B-1)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND 3.5 CORE PVC CABLE)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Conventional)
| (i) 25 kVA TRANSFORMER (4 STAR) | 7132210008 | Each | 1 | 50174 | 50174
| (ii) 63 kVA TRANSFORMER (4 STAR) | 7132210009 | Each |  |  |  | 1 | 84020 | 84020
| (iii) 100 kVA TRANSFORMER (4 STAR) | 7132210010 | Each | [6 empty] | 1 | 116682 | 116682
| (iv) 200 kVA TRANSFORMER (4 STAR) | 7132210011 | Each | [9 empty] | 1 | 204592 | 204592
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426
| 11 kV H.W | 7130820241 | No. | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole |  | Cmt | 2.1 |  |  | 2.1 |  |  | 2.1 |  |  | 2.1
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62
14 | Earthing set (Pipe earth as per drg. no.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133 | 1 | 133 | 133 | 3 | 133 | 399 | 3 | 133 | 399
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297 | 1 | 297 | 297 | 3 | 297 | 891 | 3 | 297 | 891
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63
| 16x65 mm | 7130620614 | kg | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248
| 16x140 mm | 7130620625 | kg | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244
| 16x200 mm | 7130620631 | kg | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1628 | 1628 | -- |  |  | -- |  |  | --
21 | PVC insulated 4 Core cable
i | 16 Sqmm (Armoured) | 7130311084 | Mtr | 30 | 52.156 | 1564.68 | -- | [5 empty] | --
ii | 70 Sqmm | 7130311054 | Mtr | -- |  |  | 30 | 114.082 | 3422.46 | 30 | 114.082 | 3422.46 | --
iii | 150 Sqmm | 7130311057 | Mtr | -- | [5 empty] | 10 | 394.64 | 3946.4 | 30 | 394.64 | 11839.2
iv | 300 Sqmm | 7130311061 | Mtr | [9 empty] | 10 | 626.228 | 6262.28
22 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 13758 | 13758 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 17198 | 17198
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 34396 | 34396
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8675 | 8675 | 1 | 8675 | 8675
24 | SUB TOTAL-1 |  |  |  |  | 108981.246 |  |  | 156815.026 |  |  | 206398.426 |  |  | 322239.046
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 9808.3121 |  | 0.09 | 14113.3523 |  | 0.09 | 18575.8583 |  | 0.09 | 29001.5141
26 | Service in lieu of concreting metal & sand only |  | Cmt | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
28 | Labour charges as per Sch. CL-3 |  |  |  |  | 8460.67 |  |  | 8887.44 |  |  | 8887.44 |  |  | 11027.94
29 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 4137.5359 |  |  | 4580.5306 |  |  | 4580.5306 |  |  | 4580.5306
30 | SUB TOTAL-2 |  |  |  |  | 143835.7119 |  |  | 196844.2968 |  |  | 250890.2028 |  |  | 379296.9786
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 11987.9371 |  | 0.11 | 17249.6529 |  | 0.11 | 22703.8269 |  | 0.11 | 35446.2951
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 155823.6489 |  |  | 214093.9497 |  |  | 273594.0297 |  |  | 414743.2737
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 155824 |  |  | 214094 |  |  | 273594 |  |  | 414743
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.

## C-7 (B-1) A
COST SCHEDULE C-7 (B-1) A
RELOCATION OF 25 / 63 / 100 kVA 11/0.4 kV X-MER S/S USING H- BEAM POLE AND 3.5 CORE PVC CABLE [BASED ON COST SCHEDULE C-7 (B-1) EXCEPT TRANSFORMER COST ]
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr; 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715
2 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426
4 | 11 kV H.W | 7130820241 | No. | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212
6 | 11 kV D.O. fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole |  | Cmt | 2.1 |  |  | 2.1 |  |  | 2.1 |  |  | 2.1
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
16 | Red Oxide paint | 7130211158 | Ltr | 1 | 133 | 133 | 1 | 133 | 133 | 3 | 133 | 399 | 3 | 133 | 399
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297 | 1 | 297 | 297 | 3 | 297 | 891 | 3 | 297 | 891
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | kg | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63
| 16x65 mm | 7130620614 | kg | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248
| 16x140 mm | 7130620625 | kg | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244
| 16x200 mm | 7130620631 | kg | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1628 | 1628 | -- |  |  | -- |  |  | --
21 | PVC insulated 4 Core cable
i | 16 Sqmm (Armoured) | 7130311084 | Mtr | 30 | 52.156 | 1564.68 | --
ii | 70 Sqmm | 7130311054 | Mtr | -- |  |  | 30 | 114.082 | 3422.46 | 30 | 114.082 | 3422.46
iii | 150 Sqmm | 7130311057 | Mtr | -- | [5 empty] | 10 | 394.64 | 3946.4 | 30 | 394.64 | 11839.2
iv | 300 Sqmm | 7130311061 | Mtr | [9 empty] | 10 | 626.228 | 6262.28
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 13758 | 13758 | -- |  |  | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 17198 | 17198
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 34396 | 34396
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8675 | 8675 | 1 | 8675 | 8675
24 | SUB TOTAL-1 |  |  |  |  | 58807.246 |  |  | 72795.026 |  |  | 89716.426 |  |  | 117647.046
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 5292.6521 |  | 0.09 | 6551.5523 |  | 0.09 | 8074.4783 |  | 0.09 | 10588.2341
26 | Service in lieu of concreting metal & sand only |  | Cmt | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214
27 | Service in lieu of Earthing Coal & Sand etc |  | No | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
28 | Labour charges as per Sch. CL-3 |  |  |  |  | 8460.67 |  |  | 8887.44 |  |  | 8887.44 |  |  | 11027.94
29 | Transport charges upto 50 Kms average lead from Area stores to construction camp incl. site transport (Transport Sch T-1) |  |  |  |  | 4137.5359 |  |  | 4580.5306 |  |  | 4580.5306 |  |  | 4580.5306
30 | SUB TOTAL-2 |  |  |  |  | 89146.0519 |  |  | 105262.4968 |  |  | 123706.8228 |  |  | 156291.6986
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 6468.7971 |  | 0.11 | 8007.4529 |  | 0.11 | 9868.8069 |  | 0.11 | 12941.1751
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 95614.8489 |  |  | 113269.9497 |  |  | 133575.6297 |  |  | 169232.8737
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 95615 |  |  | 113270 |  |  | 133576 |  |  | 169233

## C-7 (B-1) B
COST SCHEDULE -- C-7 (B-1) B
|  |  | RENOVATION OF EXISTING DISTRIBUTION TRANSFORMERS | [13 empty] | 2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER |  |  | 315 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19
1 | LT Distribution Box
| 25 kVA |  | No | 0 | 0 | 0
| 63 kVA | 7131950065 | No |  |  |  | 1 | 13758 | 13758
| 100 kVA | 7131950105 | No | [6 empty] | 1 | 17198 | 17198
| 200 kVA | 7131950200 | No | [9 empty] | 1 | 34396 | 34396
| 315 kVA | 7131950207 | No | [12 empty] | 1 | 45861 | 45861
2 | PVC Insulated 4 core cable
| 25 kVA (70 sq mm) | 7130311054 | Mtr | 30 | 114.082 | 3422.46
| 63 kVA (70 sq mm) | 7130311054 | Mtr |  |  |  | 30 | 114.082 | 3422.46
| 100 kVA (70 sq mm) | 7130311054 | Mtr | [6 empty] | 30 | 114.082 | 3422.46
| 100 kVA (150 sq mm) | 7130311057 | Mtr | [6 empty] | 10 | 394.64 | 3946.4
| 200 kVA (150 sq mm) | 7130311057 | Mtr | [9 empty] | 30 | 394.64 | 11839.2
| 200 kVA (300 sq mm) | 7130311061 | Mtr | [9 empty] | 10 | 626.228 | 6262.28
| 315 kVA (150 sq mm) | 7130311057 | Mtr | [12 empty] | 30 | 394.64 | 11839.2
| 315 kVA (300 sq mm) | 7130311061 | Mtr | [12 empty] | 10 | 626.228 | 6262.28
3 | Earthing set (Pipe earth as per drg no. G/008) (Material + services)
| (i) GI Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) GI Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
4 | SUB TOTAL-1 |  |  |  |  | 5827.995 |  |  | 19585.995 |  |  | 26972.395 |  |  | 54903.015 |  |  | 66368.015
5 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 524.5195 |  | 0.09 | 1762.7396 |  | 0.09 | 2427.5156 |  | 0.09 | 4941.2713 |  | 0.09 | 5973.1214
6 | Service in lieu of earthing coal & sand |  | Nos | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
7 | Labour charges as per Sch. CL-7 (B-1)B |  |  |  |  | 3510.1737 |  |  | 4141.29 |  |  | 5277.15 |  |  | 6246.08 |  |  | 6246.08
8 | Transportation charges |  | LS |  |  | 4137.5318 |  |  | 4580.5295 |  |  | 4580.5295 |  |  | 4580.5295 |  |  | 4580.5295
9 | SUB TOTAL-2 |  |  |  |  | 19826.8465 |  |  | 35897.1804 |  |  | 45084.2164 |  |  | 76497.5222 |  |  | 88994.3722
10 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 641.0794 |  | 0.11 | 2154.4594 |  | 0.11 | 2966.9635 |  | 0.11 | 6039.3317 |  | 0.11 | 7300.4816
11 | Grand Total |  |  |  |  | 20467.926 |  |  | 38051.6399 |  |  | 48051.1799 |  |  | 82536.8539 |  |  | 96294.8539
12 | Grand Total (Round off) |  |  |  |  | 20468 |  |  | 38052 |  |  | 48051 |  |  | 82537 |  |  | 96295

## C-7(B-2)
COST SCHEDULE C-7 (B-2)
11/0.4 kV OUT DOOR SUB-STATION (USING H-BEAM POLE FOR 25 / 63 / 100 / 200 kVA TRANSFORMER AND SINGLE CORE CABLE)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | 25 kVA TRANSFORMER |  |  | 63 kVA TRANSFORMER |  |  | 100 kVA TRANSFORMER |  |  | 200 kVA TRANSFORMER
|  |  |  | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Transformer 11/0.4 kV (Conventional)
| (i) 25 kVA TRANSFORMER (4 STAR) | 7132210008 | Each | 1 | 50174 | 50174
| (ii) 63 kVA TRANSFORMER (4 STAR) | 7132210009 | Each |  |  |  | 1 | 84020 | 84020
| (iii) 100 kVA TRANSFORMER (4 STAR) | 7132210010 | Each | [6 empty] | 1 | 116682 | 116682
| (iv) 200 kVA TRANSFORMER (4 STAR) | 7132210011 | Each | [9 empty] | 1 | 204592 | 204592
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715 | 816.2 | 32.575 | 26587.715
3 | DC Cross arm of 100x50 mm 8' Center | 7130810517 | No | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426 | 3 | 142 | 426
| 11 kV H.W | 7130820241 | No. | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348 | 3 | 116 | 348
5 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212 | 6 | 202 | 1212
6 | 11 kV DO fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63 | 1 | 2745.63 | 2745.63
7 | 11 kV DO Fuse unit | 7131930412 | Each | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597 | 3 | 1199 | 3597
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | kg | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72 | 20 | 33.236 | 664.72
9 | (i) Stay Set 16 mm | 7130860032 | No | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380 | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95 | 22 | 59.225 | 1302.95
| (iii) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64 | 4 | 249.66 | 998.64
10 | Concreting of supports @ 0.6 Cmt/pole & @ 0.2 Cmt/Stay & base padding @ 0.05 Cmt per pole |  | Cmt | 2.1 |  |  | 2.1 |  |  | 2.1 |  |  | 2.1
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3 | 437 | 4.9 | 2141.3
11 | Transformer belting with 50x50x6 mm angle with 2 cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024 | 34 | 33.236 | 1130.024
12 | Transformer mounting Cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1 | 1 | 3758.1 | 3758.1
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62 | 1 | 62 | 62
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611 | 9 | 179 | 1611
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535 | 15 | 52.969 | 794.535
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | 4 | 63.963 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133 | 1 | 133 | 133 | 3 | 133 | 399 | 3 | 133 | 399
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297 | 1 | 297 | 297 | 3 | 297 | 891 | 3 | 297 | 891
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551 | 3 | 517 | 1551
19 | MS Nuts & Bolts |  | Kg | 14 |  |  | 14 |  |  | 14 |  |  | 14
| 16x40 mm | 7130620609 | Kg | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63 | 1 | 63 | 63
| 16x65 mm | 7130620614 | Kg | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248 | 4 | 62 | 248
| 16x140 mm | 7130620625 | Kg | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244 | 4 | 61 | 244
| 16x200 mm | 7130620631 | Kg | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305 | 5 | 61 | 305
20 | TPN switch fuse unit (63 Amps) | 7131920254 | No | 1 | 1628 | 1628 | -- |  |  | -- |  |  | --
21 | Single Core cable
i | 16 Sqmm | 7130311008 | Mtr | 120 | 14.819 | 1778.28 | -- | [5 empty] | --
ii | 35 Sqmm | 7130310021 | Mtr | -- |  |  | 80 | 24.976 | 1998.08
iii | 50 Sqmm | 7130311009 | Mtr | -- |  |  | 40 | 34.517 | 1380.68 | 120 | 34.517 | 4142.04
iv | 70 Sqmm | 7130311010 | Mtr | [6 empty] | 40 | 46.364 | 1854.56 | 120 | 46.364 | 5563.68
v | 150 Sqmm | 7130311011 | Mtr | [9 empty] | 40 | 87.502 | 3500.08
22 | LT distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950065 | Each |  |  |  | 1 | 13758 | 13758 | --
ii | 100 kVA | 7131950105 | Each | [6 empty] | 1 | 17198 | 17198
iii | 200 kVA | 7131950200 | Each | [9 empty] | 1 | 34396 | 34396
23 | 11 kV A.B. Switch | 7131930221 | Each | -- |  |  | -- |  |  | 1 | 8675 | 8675 | 1 | 8675 | 8675
24 | SUB TOTAL-1 |  |  |  |  | 109194.846 |  |  | 156771.326 |  |  | 205026.166 |  |  | 313201.326
25 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 9827.5361 |  | 0.09 | 14109.4193 |  | 0.09 | 18452.3549 |  | 0.09 | 28188.1193
26 | Service in lieu of concreting metal & sand only |  | Cmt | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214 | 2.1 | 3153.0102 | 6621.3214
27 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264 | 1 | 5826.6264 | 5826.6264
28 | Labour Charges as per Sch CL-3 |  |  |  |  | 8460.67 |  |  | 8887.44 |  |  | 8887.44 |  |  | 11027.94
29 | Transport charges upto 50 Kms averg. lead from Area stores to construction camp inc. site transport (Transport Sch T-1) |  |  |  |  | 4137.5359 |  |  | 4580.5306 |  |  | 4580.5306 |  |  | 4580.5306
30 | SUB TOTAL-2 |  |  |  |  | 144068.5359 |  |  | 196796.6638 |  |  | 249394.4394 |  |  | 369445.8638
31 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 12011.4331 |  | 0.11 | 17244.8459 |  | 0.11 | 22552.8783 |  | 0.11 | 34452.1459
32 | Cost per S/s for non-guaranteed works |  |  |  |  | 156079.9689 |  |  | 214041.5097 |  |  | 271947.3177 |  |  | 403898.0097
33 | Cost per S/s for non-guaranteed works (Round off) |  |  |  |  | 156080 |  |  | 214042 |  |  | 271947 |  |  | 403898
Note (A) :- (1) All the rates are with considering price variation clause.
(2) As per requirement 315 kVA Transformer may be used against 200 kVA schedule
Note (B) :- A Capacitor is to be installed of appropriate capacity on the transformer in case of estimate prepared for Irrigation Pump.
ITEMS REMOVED FROM SoR 2015-16
| 11 kV G.I. Pin | 7130820155 | No

## C-8
COST SCHEDULE C-8
1 Km OF 11 kV LINE ON 365 kG 11 Mtr. LONG PCC POLE USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 METER.
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | PCC Pole using Raccoon Conductor |  | PCC Pole using Dog Conductor
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 365 Kg; 11 Mtr long PCC Pole |  | No | 4515 | 12 | 54180 | 12 | 54180
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 866.17 | 12 | 10394.04 | 12 | 10394.04
3 | Stay Clamp for PCC Pole | 7130810193 | No | 225.04 | 12 | 2700.48 | 12 | 2700.48
4 | 11 kV Top clamp | 7130810679 | No | 242.99 | 12 | 2915.88 | 12 | 2915.88
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 97 | 12 | 1164 | 12 | 1164
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 202 | 36 | 7272 | 36 | 7272
7 | ACSR Raccoon Conductor with 3% sag | 7130830060 | Mtr | 42.115 | 3100 | 130556.5
8 | ACSR Dog Conductor with 3% sag | 7130830063 | Mtr | 54.885 |  |  | 3100 | 170143.5
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 118 | 6 | 708 | 6 | 708
10 | (I) Stay set 20 mm | 7130860033 | No | 629 | 4 | 2516 | 4 | 2516
| (II) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 58.65 | 34 | 1994.1 | 34 | 1994.1
(III) Stay Clamp
| (i) Stay Clamp for PCC Pole | 7130810193 | No | 225.04 | 4 | 900.16 | 4 | 900.16
11 | Concreting of support @ 0.5 Cmt/pole, @ 0.3 Cmt/stay & base padding @ 0.05 Cmt /pole |  | Cmt |  | 7.8 |  | 7.8 |  | Earlier concreting was taken @ 0.6 Cmt / pole
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 1622.4 | 7949.76 | 1622.4 | 7949.76
12 | Red Oxide Paint | 7130211158 | Ltr | 133 | 2 | 266 | 2 | 266
13 | Aluminium Paint | 7130210809 | Ltr | 297 | 2 | 594 | 2 | 594
14 | Barbed Wire [ @ 2 Kg/Pole ] | 7130610206 | Kg | 63.963 | 24 | 1535.112 | 24 | 1535.112 | Earlier Qty. was 1 kG | because @2 kg per pole
15 | Danger Board | 7130880041 | Each | 62 | 12 | 744 | 12 | 744
16 | Binding wire and tape | 7130830006 | Kg | 130 | 6 | 780 | 6 | 780
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 63 | 1 | 63 | 1 | 63
| 16x65 mm | 7130620614 | Kg | 62 | 12 | 744 | 12 | 744
| 16x140 mm | 7130620625 | Kg | 61 | 11 | 671 | 11 | 671
18 | SUB TOTAL-1 |  |  |  |  | 228648.032 |  | 268235.032
19 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 20578.3229 |  | 24141.1529
20 | Service in lieu of concreting metal & sand only |  | Cmt | 3153.0102 | 9 | 28377.0918 | 9 | 28377.0918
21 | Labour charges as per Sch No.- CL-4 |  |  |  |  | 42588.79 |  | 43869.1
22 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 7192.9739 |  | 7192.9739 |  | 7192.9739
23 | SUB TOTAL-2 |  |  |  |  | 327385.2106 |  | 371815.3506
24 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 25151.2835 |  | 29505.8535
25 | Cost per Km for non-guaranteed works |  |  |  |  | 352536.4942 |  | 401321.2042
26 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 352536 |  | 401321
Note: All the rates are with considering price variation clause.
ITEMS REMOVED FROM Schedule- C-8 in 2016-17
1 | 60 Kg/Mtr 13.0 Mtr Long Rail pole for Raccoon conductor i.e. 780 Kg/pole x 12 Nos = 9360 Kgs | 7130601072 | Kg
12 | (III) Stay Clamp
| (i) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (ii) Stay Clamp for Rail Pole B Type | 7130810251 | No
4 | Back Clamp for Cross Arm | 7130810361 | No

## C-9
COST SCHEDULE C-9
1 KM OF 11 kV LINE ON H-BEAM 152x152 MM 37.1 Kg /MTR. 13.0 MTR. USING RACCOON / DOG CONDUCTOR MAXIMUM SPAN 80 MTR.
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | H-Beam using Raccoon conductor |  | H-Beam using Dog conductor
[5 empty] | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 12 Nos = 5788 Kgs | 7130601958 | Kg | 32.575 | 5788 | 188544.1 | 5788 | 188544.1
2 | 11 kV 'V' Cross arm with back clamp | 7130810495 | No | 866.17 | 12 | 10394.04 | 12 | 10394.04
3 | Back Clamp for Cross Arm | 7130810361 | No | 239.47 | 12 | 2873.64 | 12 | 2873.64
4 | 11 kV Top clamp | 7130810679 | No | 242.99 | 12 | 2915.88 | 12 | 2915.88
5 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 97 | 12 | 1164 | 12 | 1164
6 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 202 | 36 | 7272 | 36 | 7272
7 | ACSR Raccoon conductor with 3% sag | 7130830060 | Mtr | 42.115 | 3100 | 130556.5
8 | ACSR Dog conductor with 3% sag | 7130830063 | Mtr | 54.885 |  |  | 3100 | 170143.5
9 | Jointing Sleeves suitable for Raccoon / Dog ACSR Conductor | 7130830051 | No | 118 | 6 | 708 | 6 | 708
10 | (i) Stay set 20 mm | 7130860033 | No | 629 | 4 | 2516 | 4 | 2516
| (ii) Stay Wire 7/8 SWG @ 8.5 Kg per stay | 7130860076 | Kg | 58.65 | 34 | 1994.1 | 34 | 1994.1
(iii) Stay Clamp
| (I) Stay Clamp for "H" Beam | 7130810692 | No | 249.66 | 4 | 998.64 | 4 | 998.64
11 | Concreting of support @ 0.6 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt /pole |  | Cmt |  | 9 |  | 9
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 1872 | 9172.8 | 1872 | 9172.8
12 | Red Oxide paint | 7130211158 | Ltr | 133 | 2 | 266 | 2 | 266
13 | Aluminium Paint | 7130210809 | Ltr | 297 | 2 | 594 | 2 | 594
14 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 63.963 | 24 | 1535.112 | 24 | 1535.112 | Earlier Qty. was 1 kG | because @2 kg per pole
15 | Danger Board | 7130880041 | Each | 62 | 12 | 744 | 12 | 744
16 | Binding wire and tape | 7130830006 | Kg | 130 | 6 | 780 | 6 | 780
17 | MS Nuts and Bolts |  | Kg |  | 24 |  | 24
| 16x40 mm | 7130620609 | Kg | 63 | 1 | 63 | 1 | 63
| 16x65 mm | 7130620614 | Kg | 62 | 12 | 744 | 12 | 744
| 16x140 mm | 7130620625 | Kg | 61 | 11 | 671 | 11 | 671
18 | SUB TOTAL-1 |  |  |  |  | 364506.812 |  | 404093.812
19 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 32805.6131 |  | 36368.4431
20 | Service in lieu of concreting metal & sand only |  | Cmt | 3153.0102 | 9 | 28377.0918 | 9 | 28377.0918
21 | Labour charges as per Sch No. CL-4 |  |  |  |  | 41477.57 |  | 42757.87
22 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch T-1) |  |  | 7191.7005 |  | 7191.7005 |  | 7191.7005
23 | SUB TOTAL-2 |  |  |  |  | 474358.7874 |  | 518788.9174
24 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 40095.7493 |  | 44450.3193
25 | Cost per Km for non-guaranteed works |  |  |  |  | 514454.5367 |  | 563239.2367
26 | Cost per Km for non-guaranteed works (Rounded off) |  |  |  |  | 514455 |  | 563239
Note: All the rates are with considering price variation clause.

## C-9 (A)
COST SCHEDULE C-9 (A)
ADDITIONAL (MID SPAN) POLES FOR NEW 11 kV LINE WITH RACCOON CONDUCTOR
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | H BEAM 152X152 MM 37.10 KG / MTR 13.0 MTR LONG
|  |  |  | Qnty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm; 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole | 7130601958 | kg | 482.3 | 32.575 | 15710.9225
2 | 11 kV "V" cross arm 65x65x6 mm angle type with back cleat | 7130810495 | No | 1 | 866.17 | 866.17
3 | Cross Arm Clamp
| (i) Stay Clamp For "H" Beam | 7130810692 | No | 1 | 249.66 | 249.66
4 | 11 kV Top Clamp Angle type with cleat | 7130810679 | No | 1 | 242.99 | 242.99
5 | Earthing Set (Coil earth as per Drawing No:-G/007 | 7130870013 | No | 1 | 97 | 97
6 | 11 kV Polymeric Pin Insulator with Pin | 7130820008 | No | 3 | 202 | 606
7 | Concreting of supports H-Beam @ 0.6 Cmt. Per Pole & @ 0.2 Cmt. Per Stay and 0.05 Cmt per pole for base padding |  | Cmt. | 0.65
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 135.2 | 4.9 | 662.48
8 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 63.963 | 127.926 | Earlier Qty. was 1 kG | because @2 kg per pole
9 | Danger Board | 7130880041 | Each | 1 | 62 | 62
10 | MS Nuts and Bolts
| 16x40 mm | 7130620609 | Kg | 0.25 | 63 | 15.75
| 16x65 mm | 7130620614 | Kg | 0.6 | 62 | 37.2
| 16x140 mm | 7130620625 | Kg | 0.55 | 61 | 33.55
11 | SUB TOTAL-1 |  |  |  |  | 18711.6485
12 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 1684.0484
13 | Service in lieu of concreting metal & sand only |  | Cmt. | 0.65 | 3153.0102 | 2049.4566
14 | Labour charges as per Sch No.- CL-4 (revised based on one pole) |  |  |  |  | 1988.4772
15 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch T-1) - Taken 5% of |  |  |  |  | 359.6487
16 | SUB TOTAL-2 |  |  |  |  | 24793.2794
17 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 2058.2813
18 | Cost per Pole for non-guaranteed works |  |  |  |  | 26851.5607
19 | Cost per Pole (Rounded off) |  |  |  |  | 26852

## C-10
COST SCHEDULE C-10
AUGMENTATION OF 11/0.4 kV SUB-STATION CAPACITY (ASSUMING 25 YEARS OF LIFE & 10 YEARS IN SERVICE)
2016-17
S. No. | PARTICULARS | Bin CodeNo. | New SAP Bin Code | Unit | Rate | 25 kVA to 63 kVA |  | 63 kVA to 100 kVA |  | 100 kVA to 200 kVA
[6 empty] | Qty. | Amount | Qty. | Amount | Qty. | Amount
1 | 2 | 3 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 11/0.4 kV 63 kVA X-mer (4-STAR) |  | 7132210009 | Each | 84020 | 1 | 84020
2 | 11/0.4 kV 100 kVA X-mer (4-STAR) |  | 7132210010 | Each | 116682 |  |  | 1 | 116682
3 | 11/0.4 kV 200 kVA X-mer (4-STAR) |  | 7132210011 | Each | 204592 |  |  |  |  | 1 | 204592
4 | R.S. Joist (175X85) mm 11 Mtr. Long i.e. 19.495 kg/mtr x 11 mtr = 214.44 kg x 4 No = 857.8 Kgs |  | 7130600675 | Kg | 32.575 |  |  | 857.8 | 27942.835 | 857.8 | 27942.835
5 | (i) Stay set 16 mm | 7130860032201 | 7130860032 | No | 345 |  |  | 4 | 1380 | 4 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077103 | 7130860077 | Kg | 59.225 |  |  | 22 | 1302.95 | 22 | 1302.95
| (iii) Stay Clamp for R.S. Joist | 7130810026301 | 7130810216 | No. | 239.47 |  |  | 4 | 957.88 | 4 | 957.88
6 | Concreting of support @ 0.3 Cmt/pole, @ 0.2 Cmt/stay & base padding @ 0.05 Cmt/pole |  |  | Cmt |  |  |  | 1.5 |  | 1.5
| Cement @ 208 Kg/Cmt | 7130200401003 | 7130200401 | Kg | 4.9 |  |  | 312 | 1528.8 | 312 | 1528.8
7 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013401 | 7130870013 | No | 97 |  |  | 1 | 97 | 1 | 97
8 | Red Oxide Paint | 7130211158904 | 7130211158 | Ltr | 133 |  |  | 1 | 133 | 1 | 133
9 | Aluminium Paint | 7130210809004 | 7130210809 | Ltr | 297 |  |  | 1 | 297 | 1 | 297
10 | Barbed Wire [@ 2 Kg/Pole] | 7130407183901 | 7130610206 | Kg | 63.963 |  |  | 8 | 511.704 | 8 | 511.704 | Earlier Qty. was 2 kG | because @2 kg per pole
11 | MS Nuts & Bolts |  |  | Kg |  | 14 |  | 14 |  | 14
| 16x40 mm | 7130620609003 | 7130620609 | Kg | 63 | 1 | 63 | 1 | 63 | 1 | 63
| 16x65 mm | 7130620614003 | 7130620614 | Kg | 62 | 4 | 248 | 4 | 248 | 4 | 248
| 16x140 mm | 7130620625403 | 7130620625 | Kg | 61 | 4 | 244 | 4 | 244 | 4 | 244
| 16x200 mm | 7130620631603 | 7130620631 | Kg | 61 | 5 | 305 | 5 | 305 | 5 | 305
12 | 70 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310007 | Mtr | 39.435 | 120 | 4732.2 | 120 | 4732.2 | 120 | 4732.2
13 | 150 Sqmm Single core XLPE insulated unarmoured Al. Conductor cable |  | 7130310041 | Mtr | 97.435 |  |  |  |  | 40 | 3897.4
14 | 11 kV A.B. Switch |  | 7131930221 | Each | 8675 |  |  |  |  | 1 | 8675
15 | LT Distribution box suitable for transformer with isolator on incoming side & SPMCCB's on outgoing side
i | 63 kVA | 7131950063801 | 7131950065 | No | 13758 | 1 | 13758
ii | 100 kVA | 7131950105901 | 7131950105 | No | 17198 |  |  | 1 | 17198
iii | 200 kVA | 7131950200001 | 7131950200 | No | 34396 |  |  |  |  | 1 | 34396
16 | SUB TOTAL-1 | [5 empty] | 103370.2 |  | 173623.369 |  | 291303.769
17 | Incidental Charges @ 9% : - |  |  |  | 0.09 |  | 9303.318 |  | 15626.1032 |  | 26217.3392
18 | Labour charges as per Sch. CL-10(B) | [5 empty] | 13858.47 |  | 15810.93 |  | 17522.02
19 | Transportation charges | [5 empty] | 4137.5318 |  | 4580.5388 |  | 4580.5388
20 | SUB TOTAL-2 | [5 empty] | 130669.5198 |  | 209640.941 |  | 339623.667
21 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 |  | 11370.722 |  | 19098.5706 |  | 32043.4146
22 | SUB TOTAL-3 | [5 empty] | 142040.2418 |  | 228739.5116 |  | 371667.0816
23 | Cost of X-mer (Cost of X-mer to be taken at the time of procurement i.e before 10 years)
| (i) 25 kVA |  |  | No |  | 1 | 23760
| (ii) 63 kVA |  |  | No |  |  |  | 1 | 43064
| (iii) 100 kVA |  |  | No | [5 empty] | 1 | 54938
24 | (-) 10% Irreducible cost | [5 empty] | 2376 |  | 4306.4 |  | 5493.8
25 | (-) 10 year life @ 4% per year | [5 empty] | 8553.6 |  | 15503.04 |  | 19777.68
26 | Depreciated cost of X-mer after addition to 10% irreducible cost | [5 empty] | 15206.4 |  | 27560.96 |  | 35160.32
27 | (-) Cost of old X-mer assuming 25 years of life & 10 years in service | [5 empty] | 15206.4 |  | 27560.96 |  | 35160.32
28 | Net cost of augmentation | [5 empty] | 126833.8418 |  | 201178.5516 |  | 336506.7616
29 | Net cost of augmentation (R/Off) | [5 empty] | 126834 |  | 201179 |  | 336507
All the rates are with considering price variation clause.

## C-11
COST SCHEDULE C-11
11/0.4 kV OUT DOOR SUB-STATION (16 kVA TRANSFORMER)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | 16 kVA, 11/.4 kV X' MER
|  |  |  | Qty. | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV 16 kVA (4-STAR) Aluminium Wound | 7132210007 | No | 1 | 41602 | 41602
2 | 140 Kg 8.0 Mtr. long PCC Pole | 7130800012 | No | 3 | 1659 | 4977
3 | DC Cross arm of 100x50x6 mm 8' Center 2.7 Mtr. long | 7130810517 | No | 1 | 3758.1 | 3758.1
4 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426
5 | 11 kV Strain H/W | 7130820241 | Set | 3 | 116 | 348
6 | 11 kV D.O. Fuse & LA mounting DC Cross arm (75x40 mm) | 7130810509 | No | 1 | 2745.63 | 2745.63
7 | 11 kV D.O. Fuse unit | 7131930412 | Each | 3 | 1199 | 3597
8 | MS Angle 50x50x6 mm for X-mer Clamping set | 7130600023 | Kg | 20 | 33.236 | 664.72
9 | (i) Stay set 16 mm | 7130860032 | No | 4 | 345 | 1380
| (ii) Stay Wire 7/10 SWG @ 5.5 Kg/Stay | 7130860077 | Kg | 22 | 59.225 | 1302.95
| (iii) Stay Clamp | 7130810026 | No | 4 | 120.59 | 482.36
10 | Concreting of supports @ 0.3 Cmt/pole & @ 0.2 Cmt/Stay & base pad @ 0.05 Cmt/pole |  | Cmt | 1.85
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 385 | 4.9 | 1886.5
11 | Transformer belting with 50x50x6 mm angle with 2 Cross fixing channel. | 7130600023 | Kg | 34 | 33.236 | 1130.024
12 | Transformer mounting cross arm 100x50 mm channel. | 7130850201 | Set | 1 | 3758.1 | 3758.1
13 | Danger Board | 7130880041 | Each | 1 | 62 | 62
14 | Earthing set (Pipe earth as per drg. No.-G/008) (material + Services)
| (i) G.I.Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611
| (ii) G.I.Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535
15 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 6 | 63.963 | 383.778 | Earlier Qty. was 2 kG | because @2 kg per pole
16 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133
17 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297
18 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551
19 | MS Nuts & Bolts |  | Kg | 14
| 16x40 mm | 7130620609 | Kg | 1 | 63 | 63
| 16x65 mm | 7130620614 | Kg | 4 | 62 | 248
| 16x140 mm | 7130620625 | Kg | 4 | 61 | 244
| 16x200 mm | 7130620631 | Kg | 5 | 61 | 305
20 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 678 | 678
21 | 16 Sqmm single core PVC insulated Cable | 7130311008 | Mtr | 120 | 14.819 | 1778.28
22 | CT operated electronic static meter 100/5 Amp. | 7131310997 | No | 1 | 2027 | 2027
23 | LT CT 50/5 Amp. | 7132230016 | No | 4 | 320 | 1280
24 | Meter Box (GI plain sheet) for 3 Phase LT CT operated meter. | 7132406420 | No | 1 | 2437 | 2437
25 | Copper control cable 4 core 2.5 sq.mm Unarmoured | 7130310654 | Mtr | 12 | 58.843 | 706.116
26 | SUB TOTAL-1 |  |  |  |  | 82657.093
27 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 7439.1384
28 | Back filling of poles with boulders @ 0.3 CMT per pole. |  | No | 3 | 218.6076 | 655.8228
29 | Service in lieu of concreting metal & sand only |  | Cmt | 1.85 | 3153.0102 | 5833.0689
30 | Service in lieu of Earthing Coal & Sand etc. |  | No | 1 | 5826.6264 | 5826.6264
31 | Labour charges as per Sch. CL-3 |  |  |  |  | 8460.67
32 | Transport charges upto 50 Kms average lead from Area stores to construction camp including site transport (Transport Sch. T-1) |  |  |  |  | 4137.5359
33 | SUB TOTAL-2 |  |  |  |  | 115009.9553
34 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 9092.2802
35 | Cost per S/s for non-guaranteed works |  |  |  |  | 124102.2356
36 | Cost per S/s for non-guaranteed works (R/off) |  |  |  |  | 124102
Note: (1) All the rates are with considering price variation clause.

## C-12
COST SCHEDULE C-12
SCHEDULE FOR 11 kV UNDERGROUND CABLE CROSSING UNDER EXISTING RAILWAY TRACK / ROAD FOR 60 MTR. LONG CORRIDOR / ROUTE LENGTH OF HDPE PIPE, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL SINGLE FEEDER LINE.
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qty. | Using HDD Technique | Using Pipe Pushing Method
[6 empty] | Amount | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | HDPE Pipe 200 mm ID; 240 mm OD | 7132461004 | Mtr | 1020 | 120 | 122400 | 122400
2 | Jointing arrangement of HDPE Pipe | 7132461005 | No | 371 | 18 | 6678 | 6678 | Qty earlier was 38 No.
3 | 11 kV XLPE 240 sqmm 3 core UG Cable | 7130310079 | Mtr | 922.53 | 180 | 166055.4 | 166055.4 | Qty earlier was 160 Mtr.
4 | End terminating jointing kit for 240 sqmm XLPE cable | 7130352041 | Set | 10751 | 4 | 43004 | 43004
5 | GI pipe 200 mm for cable support at D.P. | 7130640027 | RM | 929 | 24 | 22296 | 22296 | Qty earlier was 12 Mtr. | Renamed, Earlier-- GI pipe 200 mm for 400 sqmm cable of dia 105 mm
6 | Caping of HDPE Pipe on both end of pipe using circular PVC plate of thickness 10 mm of size equivalent to O.D. of HDPE Pipe and using M-seal to avoid ingrace of moisture, insects, rats etc. to avoid damage to cable. |  | No. | 1500 | 4 | 6000 | 6000 | Earlier --Caping of HDPE Pipe on both end of pipe with Concreting and Bricks work
7 | M.S.Flat (50x6) mm | 7130600173 | kg | 34.149 | 100 | 3414.9 | 3414.9
8 | Supplying & erection of cement cable route marker with colour painting & naming the work duly embossed complete size of concrete 600 mm x 225 mm x 100 mm |  | No. | 556 | 4 | 2224 | 2224 | Earlier-- Cable marker for U/G cable
9 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 10.423 | 80 | 833.84 | 833.84 | NEW ADDED
10 | Sand | 7132498006 | Cmt | 670 | 1.2 | 804 | 804 | NEW ADDED
11 | 11 kV Polymer Lightning Arrestors | 7130840029 | Each | 517 | 6 | 3102 | 3102 | NEW ADDED
12 | Aluminium conductor Raccoon for jumpering of L.A. | 7130830060 | Mtr | 42.115 | 18 | 758.07 | 758.07 | NEW ADDED
13 | Aluminium clamp suitable for Dog / Raccoon conductor for connecting L.A | 7130830585 | No. | 223 | 6 | 1338 | 1338 | NEW ADDED
14 | GI earthing pipe 40 mm dia 3.0 mtr long, 4 mm thick with 12 mm holes at 18 places in each pipe at equal distance tapered casing at lower end. * | 7130642039 | No | 770 | 10 | 7700 | 7700
15 | Sundries for meeting out the expenses towards processing fees, submission / approval of drawing using AutoCAD obtaining permission, from railway / Road constructing authorities including liaisoning work etc. |  | LS | LS | LS | 25000 | 25000
16 | SUB TOTAL-1 |  |  |  |  | 411608.21 | 411608.21
17 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 37044.7389 | 37044.7389
18 | Service in lieu of Earthing Coal & Sand etc |  | No | 1942.2007 | 10 | 19422.0069 | 19422.0069 | NEW ADDED
19 (a) | Labour Charges for laying of HDPE Pipe (using HDD Technique ** ) as per Schedule AL-5 |  |  |  |  | 251354
(b) | Labour Charges for laying of HDPE Pipe (using Pipe Pushing Method ) as per Schedule AL-5 | [5 empty] | 1741269
20 | Labour Charges for excavation of cable trench beyond the length of HDPE Pipe upto DP Structure |  | Cmt | 187.7776 | 12 | 2253.3316 | 2253.3316 | NEW ADDED | (20 Mx1 Mx0.6 M)
21 | Transportation Charges |  |  |  |  | 60295.0195 | 60295.0195
22 | SUB TOTAL-2 |  |  |  |  | 781977.307 | 2271892.307
23 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 45276.9031 | 45276.9031
24 | Charges payable to Railway including supervision charges etc. | 15% |  |  |  | 117296.596 | 340783.846 | Name Changed Earlier-Way leave charges payable to Railway including supervision
25 | Cost per 60 Mtr for non guaranteed works |  |  |  |  | 944550.8061 | 2657953.0561
26 | Cost per 60 Mtr for non guaranteed works (Rounded off ) |  |  |  |  | 944551 | 2657953
* | 4 Nos earthings are required for cable & 6 Nos. for 2 DP's
** | Horizontal Directional Drilling (HDD) Technique
The rates mentioned at S.No.1, 2 & 3 are applicable for 60 Mtr Corridor of Railway crossing. Estimate may be prepared based on actual length of corridor.
*** | The charges to be paid for according railway permission shall be made as per actuals i.e. based on the demand note / payment received for the same.
ITEMS REMOVED FROM Schedule- C-12 in 2016-17
6 | GI bend 200 mm | 7130640028 | No
Note on E15: 89326879: Assuming 2 kg M-seal @ Rs 450/- per kg + PVC Plate 10 mm thick
***

## C-12 (A)
COST SCHEDULE C-12 (A)
SCHEDULE FOR 11 kV UNDERGROUND CABLE ROAD CROSSING FOR 50 MTR. LENGTH, UNDER 2.5 MTR. DEEP FROM GROUND LEVEL
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | Rate | Qnty. | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RCC pipe Type NP - 3 (2.5 mtr long)
i | 600 mm | 7130640030 | Each | 3857 | 50 | 192850
ii | 900 mm | 7130640036 | Each | 7661
2 | 11 kV 3 Core 240 sqmm XLPE UG Cable | 7130310079 | Mtr | 922.53 | 50 | 46126.5
3 | 11 kV Jointing and cable termination kit for 240 sqmm XLPE cable | 7130352041 | Set | 10751 | 2 | 21502
4 | Cable separator in RCC pipe with Angle Cross of 50x50x6 mm Angle @ 2 No. in one pipe |  | No | 495 | 40 | 19800
5 | G.I. Pipe 200 mm for 400 sq.mm Cable of dia. 105 mm | 7130640027 | RM | 929 | 12 | 11148
6 | GI bend 200 mm | 7130640028 | No | 805 | 2 | 1610
7 | Caping of RCC pipe on both end of pipe with Concreting and Bricks work |  | Cmt | 3220 | 0.5 | 1610
8 | Sundries (Please specify the items) |  | LS | LS | LS | 2200
9 | SUB TOTAL-1 |  |  |  |  | 296846.5
10 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 26716.185
11 | Labour Charges as per Schedule CL-10 (Schedule is for 1 km line, same has been revised as per 50 Mtrs.) |  |  |  |  | 9799.6565
12 | SUB TOTAL-2 |  |  |  |  | 333362.3415
13 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 32653.115
14 | Municipality Charges for reinstatement of Road as per Nagar Nigam | LS |  |  |  | 112000
15 | Cost per 50 Mtr for non guaranteed works |  |  |  |  | 478015.4565
16 | Total (Round Off) |  |  |  |  | 478015
17 | Transportation Charges as per Schedule |  |  |  |  | 72354.0235
18 | Grand Total |  |  |  |  | 550369.0235
19 | Grand Total (Round Off) |  |  |  |  | 550369

## C-13
COST SCHEDULE C-13
SINGLE POLE MOUNTED LOW CAPACITY THREE PHASE 11/0.4 kV DISTRIBUTION TRANSFORMER SUB-STATION
2016-17
S. No. | PARTICULARS | Bin Code No | Unit | Qty. | 16 kVA Three Phase |  | Single Pole Mounted 5 kVA & 10 kVA 11/0.4 kV X-mer S/s has been DELETED
[5 empty] | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | Transformer 11/0.4 kV (Conventional) [4 STAR] | 7132210007 | No. | 1 | 41602 | 41602
2 | 200 Kg 8.0 Meter long PCC Pole | 7130800033 | No. | 1 | 1782 | 1782
3 | 11 kV 'V' Cross arm with clamp (instead of DC Cross arm) | 7130810495 | No | 1 | 866.17 | 866.17
4 | 11 kV Top clamp with cleat | 7130810679 | No | 1 | 242.99 | 242.99
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 3 | 202 | 606
6 | 11 kV Polymer Disc Insulator | 7130820010 | No | 3 | 142 | 426
7 | 11 kV Strain Hardware | 7130820241 | No | 3 | 116 | 348
8 | 11 kV D.O. Fuse and L.A. mounting DC channel size 75x40x6 mm length 860 mm | 7130810509 | No | 1 | 2745.63 | 2745.63
9 | 11 kV D.O. Fuse unit for Three phase X-mer | 7131930412 | Each | 3 | 1199 | 3597
10 | MS angle for transformer clamping set size 50x50x6 mm | 7130600023 | Kg | 20 | 33.236 | 664.72
11 | (i) Stay set 16 mm | 7130860032 | No | 4 | 345 | 1380
| (ii) Stay wire 7/10 SWG @ 5.5 Kg per stay | 7130860077 | Kg | 22 | 59.225 | 1302.95
| (iii) Stay clamp | 7130810026 | No | 4 | 120.59 | 482.36
12 | Concreting of supports @ 0.5 Cmt per pole and @ 0.2 Cmt per stay & base padding @ 0.05 Cmt/pole |  | Cmt | 1.35
| Cement @ 208 kg per Cmt | 7130200401 | Kg | 281 | 4.9 | 1376.9
13 | Transformer mounting DC Cross arm size 65x65x6 channel length 800 mm |  | Set. | 1 | 1452.6579 | 1452.6579
14 | Bracket angle for Transformer mounting supports size 50x50x6 mm length 645 mm |  | No. | 2 | 688.351 | 1376.7019
15 | Danger Board | 7130880041 | Each | 1 | 62 | 62
16 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 2 | 63.963 | 127.926 | Earlier Qty. was 1 kG | because @2 kg per pole
17 | Earthing set (pipe earth as per drawing)
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 9 | 179 | 1611
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 15 | 52.969 | 794.535
18 | Red Oxide Paint | 7130211158 | Ltr | 1 | 133 | 133
19 | Aluminium Paint | 7130210809 | Ltr | 1 | 297 | 297
20 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551
21 | M.S. Nuts and Bolts
| (i) 16x40 mm | 7130620609 | Kg | 1 | 63 | 63
| (ii) 16x65 mm | 7130620614 | Kg | 4 | 62 | 248
| (iii) 16x140 mm | 7130620625 | Kg | 4 | 61 | 244
| (iv) 16x200 mm | 7130620631 | Kg | 5 | 61 | 305
22 | TPN switch fuse unit (32 Amps) | 7131920253 | No | 1 | 678 | 678
23 | GI pipe size 1 inch. for movement of LT cable from X-mer |  | Mtr. | 10 | 181.0895 | 1810.8953
24 | XLPE insulated 4 core 16 sq mm armoured cable for 3 phase X-mer | 7130311084 | Mtr. | 30 | 52.156 | 1564.68
25 | LT Feeder Piller box 1 phase 8 Way for distribution of service connection | 7130890004 | No. | 1 | 3858 | 3858
26 | SUB TOTAL-1 |  |  |  |  | 73600.1161
27 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 6624.0105
28 | Back filling of poles with boulders @ 0.3 Cmt per pole. |  | No. | 1 | 218.6076 | 218.6076
29 | Service in lieu of concreting metal and sand |  | Cmt | 1.35 | 3153.0102 | 4256.5638
30 | Labour charges as per Schedule No. CL-8 (G-1) |  |  |  |  | 5848.85
31 | Transport charges upto 50 Kms. Average lead from area store to const. camping site transport |  |  |  |  | 2387.6828
32 | SUB TOTAL-2 |  |  |  |  | 92935.8307
33 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 8096.0128
34 | Cost per Km. for Non-guaranteed works |  |  |  |  | 101031.8435
35 | Cost per Km. for Non-guaranteed works (Rounded off) |  |  |  |  | 101032

## C-14
COST SCHEDULE C-14
2016-17
PLINTH MOUNTED 11/0.4 kV OUTDOOR SUB-STATION
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | 63 kVA X-MER |  | 100 kVA X-MER |  | 200 kVA X-MER
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | RS Joist (175X85) mm 11 Mtr Long i.e. 19.495 Kg/mtr x 11 mtr. = 214.44 kg x 2 No = 428.89 Kgs | 7130600675 | Kg | 32.575 | 429 | 13974.675 | 429 | 13974.675
2 | H-BEAM 152x152 mm 37.1 Kg /Mtr 13.0 Mtr long i.e. 482.3 Kg/pole x 2 Nos = 964.6 Kgs | 7130601958 | Kg | 32.575 |  |  |  |  | 964.6 | 31421.845
3 | Transformer 11/0.4 kV (Conventional)
| 63 kVA (4-STAR) | 7132210009 | Each | 84020 | 1 | 84020
| 100 kVA (4-STAR) | 7132210010 | Each | 116682 |  |  | 1 | 116682
| 200 kVA (4-STAR) | 7132210011 | Each | 204592 |  |  |  |  | 1 | 204592
4 | DC Cross arm 100x50 mm 8' Centre | 7130810517 | No | 3758.1 | 1 | 3758.1 | 1 | 3758.1 | 1 | 3758.1
5 | 11 kV Polymer Disc Insulator | 7130820010 | No | 142 | 3 | 426 | 3 | 426 | 3 | 426
| 11 kV H.W. | 7130820241 | No | 116 | 3 | 348 | 3 | 348 | 3 | 348
6 | 11 kV DO fuse & LA mounting DC cross arm (75 x 40 mm) | 7130810509 | No | 2745.63 | 1 | 2745.63 | 1 | 2745.63 | 1 | 2745.63
7 | 11 kV DO Fuse Unit | 7131930412 | Each | 1199 | 3 | 3597 | 3 | 3597 | 3 | 3597
8 | M.S. Angle 50x50x6 mm | 7130600023 | Kg | 33.236 | 20 | 664.72 | 20 | 664.72 | 20 | 664.72
9 | (i) Stay set 16 mm | 7130860032 | No | 345 | 4 | 1380 | 4 | 1380 | 4 | 1380
| (ii) Stay wire 7/10 SWG (7.5 Kg each) | 7130860077 | Kg | 59.225 | 30 | 1776.75 | 30 | 1776.75 | 30 | 1776.75
| (iii) Stay clamp for R.S.Joist | 7130810216 | No | 239.47 | 4 | 957.88 | 4 | 957.88
| (iv) Stay clamp for H-Beam | 7130810692 | No | 249.66 |  |  |  |  | 4 | 998.64
10 | Concreting of support [0.3 Cmt per RSJ, 0.5 Cmt per H-Beam, 0.2 Cmt per stay, 9 cub.m. (1.5x1.5x4 m) for X-mer plinth] |  | Kg. |  | 10.4 |  | 10.4 |  | 10.8
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 2163 | 10598.7 | 2163 | 10598.7 | 2250 | 11025
11 | Danger Board | 7130880041 | Each | 62 | 1 | 62 | 1 | 62 | 1 | 62
12 | Earthing set pipe carth
| (i) G.I. Pipe 40 mm | 7130641396 | Mtr | 179 | 9 | 1611 | 9 | 1611 | 9 | 1611
| (ii) G.I. Wire 8 SWG | 7130870043 | Kg | 52.969 | 15 | 794.535 | 15 | 794.535 | 15 | 794.535
13 | Barbed Wire [@ 2 Kg/Pole] | 7130610206 | Kg | 63.963 | 4 | 255.852 | 4 | 255.852 | 4 | 255.852 | Earlier Qty. was 2 kG | because @2 kg per pole
14 | Red Oxide Paint | 7130211158 | Ltr | 133 | 2 | 266 | 2 | 266 | 2 | 266
15 | Aluminium Paint | 7130210809 | Ltr | 297 | 2 | 594 | 2 | 594 | 2 | 594
16 | 11 kV Polymer Lightning Arrestor | 7130840029 | Each | 517 | 3 | 1551 | 3 | 1551 | 3 | 1551
17 | M.S. Nuts & Bolts |  |  |  | 14 |  | 14 |  | 17
| 16x40 mm | 7130620609 | Kg | 63 | 1 | 63 | 1 | 63 | 1 | 63
| 16x65 mm | 7130620614 | Kg | 62 | 4 | 248 | 4 | 248 | 4 | 248
| 16x140 mm | 7130620625 | Kg | 61 | 4 | 244 | 4 | 244 | 5 | 305
| 16x200 mm | 7130620631 | Kg | 61 | 5 | 305 | 5 | 305 | 7 | 427
18 | PVC insulated 3.5 Core Cable
| 70 sqmm | 7130311054 | Mtr | 114.082 | 40 | 4563.28 | 30 | 3422.46
| 150 sqmm | 7130311057 | Mtr | 394.64 |  |  | 10 | 3946.4 | 30 | 11839.2
| 300 sqmm | 7130311061 | Mtr | 626.228 |  |  |  |  | 10 | 6262.28
19 | LT Distribution Box for X-mer
| 63 kVA | 7131950065 | No. | 13758 | 1 | 13758
| 100 kVA | 7131950105 | No. | 17198 |  |  | 1 | 17198
| 200 kVA | 7131950200 | No. | 34396 |  |  |  |  | 1 | 34396
20 | Stay Clamp for (i) R.S.Joist 175x85 mm | 7130810216 | No. | 239.47 | 14 | 3352.58 | 14 | 3352.58
| (ii) Stay clamp for H-Beam | 7130810692 | No. | 249.66 |  |  |  |  | 14 | 3495.24
21 | 11 kV AB Switch | 7131930221 | Each | 8675 |  |  | 1 | 8675 | 1 | 8675
22 | ACSR Conductor Rabbit | 7130830057 | Mtr | 28.44 | 30 | 853.2 | 30 | 853.2 | 30 | 853.2
23 | SUB TOTAL-1 |  |  |  |  | 152768.902 |  | 200351.482 |  | 334431.992
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 13749.2012 |  | 18031.6334 |  | 30098.8793
25 | Labour Charges as per Sch. CL-9. |  |  |  |  | 18312.28 |  | 20216.82 |  | 22188.49
26 | Service in lieu of concreting @ 3153.01 per Cmt. |  |  | 3153.0102 | 10.4 | 32791.3061 | 10.4 | 32791.3061 | 10.8 | 34052.5102
27 | Transportation Charges |  |  |  |  | 5730.4387 |  | 5730.4387 |  | 6685.5118
28 | SUB TOTAL-2 |  |  |  |  | 223352.1279 |  | 277121.6801 |  | 427457.3832
29 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 16804.5792 |  | 22038.663 |  | 36787.5191
30 | Grand Total |  |  |  |  | 240156.7071 |  | 299160.3431 |  | 464244.9023
31 | Total (rounding off) |  |  |  |  | 240157 |  | 299160 |  | 464245

## C-15
COST SCHEDULE C-15
SCHEDULE FOR LAYING OF 1 Km LENGTH OF 11 kV, 3 CORE 95 SQMM / 240 SQMM / 400 SQMM UNDERGROUND CABLE
2016-17
S. No. | PARTICULARS | New SAP Bin code No. | UNIT | RATE | 3x95 Sqmm CABLE |  | 3x240 Sqmm CABLE |  | 3x400 Sqmm CABLE
[5 empty] | Qty | Amount | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | 11 kV 3 Core XLPE Cable 3x95 sqmm | 7130310077 | Km | 510601 | 1 | 510601
| 11 kV 3 Core XLPE Cable 3x240 sqmm | 7130310079 | Km | 922530 |  |  | 1 | 922530
| 11 kV 3 Core XLPE Cable 3x400 sqmm | 7130310080 | Km | 1421382 |  |  |  |  | 1 | 1421382
2 | Straight through jointing kits HS type suitable for
| 95 Sqmm cable | 7130352039 | Set | 8701 | 3 | 26103
| 240 Sqmm cable | 7130352041 | Set | 10751 |  |  | 3 | 32253
| 400 Sqmm cable | 7130352042 | Set | 11000 |  |  |  |  | 3 | 33000
3 | Cable termination Kit outdoor/indoor HS type suitable for
| 95 Sqmm | 7130352043 | Set | 2406 | 2 | 4812
| 240 Sqmm | 7130352044 | Set | 2561 |  |  | 2 | 5122
| 400 Sqmm | 7130352045 | Set | 2630 |  |  |  |  | 2 | 5260
4 | Cable covering tiles 250x250x40 mm | 7130201343 | No | 10.423 | 4000 | 41692 | 4000 | 41692 | 4000 | 41692
5 | Sand | 7132498006 | Cu mtr | 670 | 60 | 40200 | 60 | 40200 | 60 | 40200
6 | M.S. Pipe 200 mm dia for drain crossing cable rarifly etc. | 7130640037 | RM (light) | 862 | 8 | 6896 | 8 | 6896 | 8 | 6896
7 | Route & joint indicating stones | 7130200204 | No | 157 | 30 | 4710 | 30 | 4710 | 30 | 4710
8 | SUB TOTAL-1 |  |  |  |  | 635014 |  | 1053403 |  | 1553140
9 | Labour Charges as per CL-10 |  |  |  |  | 195993.13 |  | 195993.13 |  | 195993.13
10 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 57151.26 |  | 94806.27 |  | 139782.6
11 | Transportation Charges @ 5% of material |  |  |  |  | 38288.1815 |  | 63514.9545 |  | 93646.6067
12 | SUB TOTAL-2 |  |  |  |  | 926446.5715 |  | 1407717.3545 |  | 1982562.3367
13 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 69851.54 |  | 115874.33 |  | 170845.4
14 | Grand Total |  |  |  |  | 996298.1115 |  | 1523591.6845 |  | 2153407.7367
15 | Grand Total (Rounded off) |  |  |  |  | 996298 |  | 1523592 |  | 2153408

## C-16
COST SCHEDULE C-16
D.T. CAPACITORS ON EXISTING DTR's OTHER THAN INDUSTRIAL (RETAINED & SHIFTED)
2016-17
S. No. | PARTICULARS | New SAP Bin code No. | Capacitor Rating - KVAR | Capacitor cost | Incidental Charges | Labour Charge per Capacitor Bank | Cost per Package | Cost per Package Round Off
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | LT Capacitor for 25 kVA DT | 7132200812 | 5 | 1637 | 147.33 | 200 | 1984.33 | 1984
2 | LT Capacitor for 63 kVA DT | 7132200813 | 10 | 3272 | 294.48 | 200 | 3766.48 | 3766
3 | LT Capacitor for 100 kVA DT | 7132200814 | 12 | 3932 | 353.88 | 200 | 4485.88 | 4486
4 | LT Capacitor for 200 kVA DT | 7132200814 | 12 | 3932 | 353.88 | 200 | 4485.88 | 4486
5 | LT Capacitor for 315 kVA DT | 7132200814 | 12 | 3932 | 353.88 | 200 | 4485.88 | 4486
| Incidental Charges @ 9% : - |  |  | 9%

## C-17
COST SCHEDULE C-17
11 kV MEDP STRUCTURE ON H-BEAM POLE, 11 METER LONG (TO BE SUPPLEMENTED FOR H.T. CONNECTION)
2016-17
S. No. | PARTICULARS | New SAP Bin Code | Unit | H-Beam 152X152 mm 37.1 Kg/Mtr 11.0 Mtr Long
|  |  |  | Qty | Rate | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | H-BEAM 152x152 mm 37.1 Kg /Mtr 11.0 Mtr long i.e. 408.1 Kg/pole x 2 Nos = 816.2 Kgs | 7130601965 | Kg | 816.2 | 32.575 | 26587.715
2 | DC Cross Arm of 100x50 mm channel (2.7 Mtr. Long) | 7130810512 | Set | 2 | 3256.41 | 6512.82
3 | 11 kV Polymer Disc Insulator | 7130820010 | No | 6 | 142 | 852
4 | 11 kV Strain H.W. fitting | 7130820241 | No | 6 | 116 | 696
5 | 11 kV Polymeric Pin insulator with Pin | 7130820008 | No | 6 | 202 | 1212
6 | (I) Stay set 16 mm | 7130860032 | No | 2 | 345 | 690
| (II) Stay Wire 7/10 SWG @ 8.5 Kg per stay | 7130860077 | Kg | 17 | 59.225 | 1006.825
(III) Stay Clamp
| (i) Stay Clamp for "H" Beam | 7130810692 | No | 4 | 249.66 | 998.64
7 | Concreting of pole @ 0.6 Cmt and 0.2 Cmt per stay and 0.05 Cmt for base padding |  | Cmt | 1.7
| Cement @ 208 Kg/cmt | 7130200401 | Kg | 353.6 | 4.9 | 1732.64
8 | Earthing Set (Coil earth as per Drawing No.-G/007) | 7130870013 | No | 2 | 97 | 194
9 | Red Oxide Paint | 7130211158 | Ltr | 2 | 133 | 266
10 | Aluminium Paint | 7130210809 | Ltr | 2 | 297 | 594
11 | Barbed wire [@ 2 Kg/Pole] | 7130610206 | Kg | 4 | 63.963 | 255.852 | Earlier Qty. was 7 kG | because @2 kg per pole
12 | Danger Board | 7130880041 | Each | 1 | 62 | 62
13 | MS Nuts and Bolts |  | Kg | 6
| 16x40 mm | 7130620609 | Kg | 0.5 | 63 | 31.5
| 16x200 mm | 7130620631 | Kg | 5.5 | 61 | 335.5
14 | GI earthing pipe of 40 mm dia. & 2.4 mm thick 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end. | 7130642039 | No | 2 | 770 | 1540
15 | G.I.Bend of 40 mm dia. |  | Each | 1 | 90 | 90
16 | 11 kV Polymer type Lightning Arrestor | 7130840029 | Each | 3 | 517 | 1551
17 | 11 kV CTPT unit of appropriate capacity |  | No
18 | Copper control cable 10 Core 2.5 Sqmm. (armoured) | 7130310660 | Mtr | 10 | 144.477 | 1444.77
19 | H.T. Static Trivector Meter 3 Ø 4 Wire 0.5 S with DLMS Protocol category A | 7131310033 | No | 1 | 3434 | 3434
20 | Universal Meter Box for HT meters. | 7132406425 | Each | 1 | 2553 | 2553
21 | Test terminal Box (TTB) | 7131310037 | Each | 1 | 870 | 870
22 | SUB TOTAL-1 |  |  |  |  | 53510.262
23 | Incidental Charges @ 9% : - |  |  |  | 0.09 | 4815.9236
24 | Service in lieu of concreting metal & sand only |  | Cmt | 1.7 | 3153.0102 | 5360.1173
25 | Labour charges as per Sch No.- CL-5 |  |  |  |  | 7421.49
26 | Transport charges upto 50 Kms average lead from Area stores to construction camp inc. site transport (Transport Sch. T-1) |  |  |  |  | 2729.7581
27 | SUB TOTAL-2 |  |  |  |  | 73837.551
28 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  |  | 0.11 | 5886.1288
29 | Cost per DP for non-guaranteed works |  |  |  |  | 79723.6799
30 | Cost per DP for non-guaranteed works (Rounded off) |  |  |  |  | 79724
Note:- All the rates are with considering price variation clause.
ITEMS REMOVED FROM Schedule- C-17 in 2016-17
2 | 60 Kg/Mtr 11.0 Mtr long Rail Pole (660 Kg each) x 2 No = 1320 Kgs | 7130601072 | Kg
7 | (III) Stay Clamp
| (ii) Stay Clamp for Rail Pole A Type | 7130810201 | No
| (iii) Stay Clamp for Rail Pole B Type | 7130810251 | No

## C-18
COST SCHEDULE C-18
2016-17
SCHEDULE FOR NEW AUTOMATED 11 KV CAPACITOR BANK AT 33/11 KV SUB-STATIONS
S. No. | PARTICULARS | Bin Code No. | Unit | Rate | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank |  | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type, Capacitor bank
[5 empty] | Qty | Amount | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9
1 | 12.1 kV,1815 kVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar+ 726 Kvar 12.1 KV. Bank shall be complete with Capacitor units of 121 KVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Botls etc. | 7132200826 | Nos | 179969 | 1 | 179969
2 | 12.1 kV,1089 KVAr, 3-Phase, 50 Hz, Outdoor Type , Capacitor bank having step as 363 Kvar + 726 Kvar 12.1 KV . Bank shall be complete with Capacitor units of 121 kVAr at 6.98 KV, including allied material such as suitable size of Aluminium busbars, Pin/Post insulators, Expulsion fuses, Cable Jointing Kit, Nuts & Bolts etc. | 7132200014 | Mtr. | 136101 |  | 0 | 1 | 136101
3 | 11 kV, Aluminium Wound, Dry type Series reactors
4 | 0.2% Reactor suitable for 363 Kvar step |  | Set | 6609.23 | 3 | 19827.69 | 3 | 19827.69
5 | 0.2% Reactor suitable for 726 Kvar step |  | Set | 8068.68 | 6 | 48412.08 | 3 | 24206.04
6 | 11 kV, 3-Phase Oil-Cooled RVT |  | No. | 40128 | 1 | 40128 | 1 | 40128
7 | 12 kV, Outdoor type Vacuum Capacitor switches |  | Nos. | 65219.24 | 3 | 195657.72 | 2 | 130438.48
8 | 11 kV, 400 Amp, Off Load Isolator with earth switch and mounting GI structure |  | Set | 26773 | 1 | 26773 | 1 | 26773
9 | Mounting GI structure for above isolator |  | Set | 13379.1 | 1 | 13379.1 | 1 | 13379.1
10 | 9 KV, 10 KA, Station Class, Polymer Lightning Arrestors | 7130840029 | set of 3 | 1551 | 1 | 1551 | 1 | 1551
| Indoor Type Automatic Control Unit along with APFC Relay |  | No. | 44956.81 | 1 | 44956.81 | 1 | 44956.81
11 | GI Structure for complete Equipment |  | Kgs. | 77.35 | 1000 | 77350 | 800 | 61880
12 | Unarmoured Control cable 8Cx2.5 Sqmm and junction box | 7130310658 | Mtr | 106.359 | 120 | 12763.08 | 120 | 12763.08 | Earlier- Armoured Control cable 16Cx2.5 Sqmm
13 | Unarmoured Control cable 10Cx2.5 Sqmm | 7130310660 | Mtr | 132.115 | 60 | 7926.9 | 60 | 7926.9 | Earlier- Armoured Control cable 10Cx2.5 Sqmm
14 | Unarmoured Control cable 2Cx2.5 Sqmm | 7130310652 | Mtr | 35.395 | 60 | 2123.7 | 60 | 2123.7 | Earlier- Armoured Control cable 2Cx2.5 Sqmm
15 | 11 KV VCB , 630 A, suitable for Capacitor Switching | 7131941762 | Nos. | 108176 | 1 | 108176
16 | 11 KV VCB , 400 A, suitable for Capacitor Switching | 7131941762 | Nos. | 108176 |  |  | 1 | 108176
17 | C & R Panel for VCB | 7131960008 | Nos. | 26331 | 1 | 26331 | 1 | 26331
18 | 11 KV Power Cable, HT XLPE, 120 Sq MM | 7130310078 | Mtr | 761.409 | 15 | 11421.135
19 | 11 KV Power Cable, HT XLPE, 95 Sq MM | 7130310077 | Mtr | 510.601 |  |  | 15 | 7659.015
20 | 11 kV C.T. 200-100/5 Amps. | 7132230185 | Nos. | 9356 | 3 | 28068 | 3 | 28068 | CT used was for Current Transformers for VCB. (200/100/5 A) LT; Now changed with 11 kV
21 | Earthing through | [7 empty] | Earlier- Earthing through MS flat & GI pipe (Set of 8 earthings)
(i) | 25 mm dia 2500 mm long GI rod earth electrodes | 7130642041 | No | 3914 | 3 | 11742 | 3 | 11742
(ii) | M.S.Flat 50 x 6 mm | 7130600173 | Kg | 34.149 | 100 | 3414.9 | 100 | 3414.9
22 | Concreting of structure |  | Cmt
| (i) Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 2059.2 | 10090.08 | 2059.2 | 10090.08
23 | SUB TOTAL-1 |  |  |  |  | 870061.195 |  | 717535.795
24 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 78305.5075 |  | 64578.2216
25 | Labour Charges |  |  |  |  | 43503.0598 |  | 35876.7898
26 | Transport Charges |  |  |  |  | 26101.8358 |  | 21526.0739
27 | Service in lieu of Concreting metal & sand only |  | Cmt | 3153.0102 | 9.9 | 31214.801 | 9.9 | 31214.801
28 | Service in lieu of Earthing Coal & Salt etc |  | No | 1942.2007 | 1 | 1942.2007 | 1 | 1942.2007
29 | SUB TOTAL-2 |  |  |  |  | 1051128.5998 |  | 872673.8818
30 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 95706.7315 |  | 78928.9374
31 | GRAND TOTAL |  |  |  |  | 1146835.3313 |  | 951602.8193
32 | GRAND TOTAL (Round Off) |  |  |  |  | 1146835 |  | 951603
ITEMS REMOVED FROM Schedule- C-18 in 2016-17
20 | Current Transformers for VCB. (200/100/5 A) | 7132230019 | Nos.

## C-19
COST SCHEDULE C-19
SCHEDULE FOR INSTALLATION OF COMPACT R.M.U. 11 kV CLASS SF6 / VCB TYPE (1 INCOMING + 2 BREAKER + 1 OUTGOING)
2016-17
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | RMU (4 Way), One Incoming + Two Breakers + One Outgoing (2OD + 2 VL), 350 MVA, 630 Amps. |  | No | 1050370 | 1 | 1050370
2 | Concreting of RMU Bed with CC 1:3:6 as per Labour Charges |  | Cmt |  | 0.37
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 76.96 | 377.104
3 | Concreting of Foundation with Reinforcement CC 1:3:6 as per Labour Charges |  | Cmt |  | 1.44
| Cement @ 208 Kg/Cmt | 7130200401 | Kg | 4.9 | 299.52 | 1467.648
4 | M.S.Strip 25 x 3 mm for earthing (of length 2 x 5 = 10 Mtr.) |  | Kg | 33.24 | 6 | 199.44
| GI earthing pipe of 40 mm dia 3.04 mtr long with 12 mm hole at 18 places at equal distance trapered casing at lower end . | 7130642039 | No | 770 | 2 | 1540
5 | SUB TOTAL-1 |  |  |  |  | 1053954.192
6 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 94855.8773
7 | Labour Charges as per Sch. CL-11. |  |  |  |  | 6104
8 | Service in lieu of Concreting metal & sand only |  | Cmt | 3153.0102 | 1.81 | 5706.9485
9 | Transportation Charges |  |  |  |  | 5730.4314
10 | SUB TOTAL-2 |  |  |  |  | 1166351.4491
11 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 115934.9611
12 | Grand Total |  |  |  |  | 1282286.4102
13 | Grand Total (Rounded off) |  |  |  |  | 1282286
MESH EARTING OF ADDL. PTR AT 33/11KV SUB-STATION (BLACK COTTON SOIL/MURRUM SOIL/HARD ROCK WITH BORE & CHEM ROD)
| 11 kV 3 Core XLPE Cable 3x240 sqmm | 7130310079 | Km | 922530 | 1 | 922530

## C-20
COST SCHEDULE C-20
SCHEDULE FOR CHEMICAL EARTHING OF METERING EQUIPMENT INSTALLED IN THE PREMISES OF HT CONSUMERS IN NORMAL / HARD ROCK SOIL
2016-17
S. No. | PARTICULARS | New SAP Bin code No. | Unit | Rate | Qty | Amount
1 | 2 | 3 | 4 | 5 | 6 | 7
1 | M.S.Strip 25x3 mm (0.6 kg/Mtr.) |  | Kg | 33.24 | 10 | 332.4
2 | Chem Rod Earthing electrode (Chemical Earthing) |  | No. | 9000 | 1 | 9000
3 | G.I. Nuts & Bolts 16x40 mm | 7130620133 | Kg | 87 | 1.5 | 130.5
4 | G.I. Nuts & Bolts 16x65 mm | 7130620140 | Kg | 87 | 1.5 | 130.5
5 | G.I. Spring Washer | 7130622922 | Kg | 125 | 1 | 125
6 | SUB TOTAL-1 |  |  |  |  | 9718.4
7 | Incidental Charges @ 9% : - |  |  | 0.09 |  | 874.656
8 | Labour Charges |  | No. | 746.84 | 1 | 746.84
9 | Transportation Charges |  |  |  |  | 800
10 | SUB TOTAL-2 |  |  |  |  | 12139.896
11 | Overhead Charges @ 11% [Market Fluctuation, Service Tax, Contractor's profit etc.] |  |  | 0.11 |  | 1069.024
12 | Grand Total |  |  |  |  | 13208.92
13 | Grand Total (Rounded off) |  |  |  |  | 13209
Note:- | Chemical Earthing consists of Galvanized Mild Steel pipe of size 2000 mm x 50 mmn Outer diameter or higher size as per site conditions, filled with a highly conductive material and a GI Strip minimum 16 mm x 3 mm covering total of pipe, forming the electrode for obtaining earth resistance less than 1 ohm.